## Cover Sheet
Sludge Handling Model for the Life Cycle Assessment of Legacy and Upgraded Wastewater Treatment Plants, Bath, NY
Version 2, 5/8/2017
Summary
This workbook contains calculations related to anaerobic digestion, compost of biosolids, and land application. Three main feedstock scenarios are set up in this workbook with the additional option to create a custom scenario. Each feedstock scenario can be paired with one of three sets of assumptions for anaerobic digester operational performance (low, base, and high). The workbook dynamically recalculates relevant input, output, and emission values based on scenario selection. The workbook was used to calculate LCI values used in the anaerobic digester sensitivity analysis and is meant as a tool for exploring feedstock options for co-digestion and composting.
Color Coding
The following system of color coding is used throughout the workbook. If using the standard scenarios only the scenario selection cells need to be specified by the user. All other parameters are specified for each scenario as detailed in the 'AD Scenarios' sheet.
|  | Set Prior to each run. | Click to jump to scenario selector
Changing value will alter results. Assumed to be standard across scenarios.
Calculated value. Don't change.
Reference value only, not used in calculations.
LCI value, expressed per cubic meter of wastewater treated.
| Sheet | Description
| AD Scenarios | Lists basic parameters for the assessed feedstock scenarios, anaerobic digester operation, expected biogas yield, and basic biogas composition
| AD Design Info | Main sheet for data entry. Allows user to specify scenario and provides the option to customize certain operational assumptions such as feedstock mix, percent volatile solids reduction, and assumed biogas yield using the custom scenario. The sheet also details initial calculations pertaining to the selected feedstock mixture
| AD CAPDET | This worksheet performs dewatering calculations and then implements the calculations associated with anaerobic digester operation generating input and output values relevant to the LCA of anaerobic digestion
| Composting & Land Application | This worksheet details composting assumptions, allows the user to select customized compost amendments, and generates input and output values relevant to the LCA of biosolids composting and land application
| Composting Emissions | Summary table listing the composting emission factors used in the low, base, and high compost emission scenarios
| AD Return Flow | Estimates increased loading of BOD and N to headworks from AD and BFP due to medium and high feedstock scenarios
| Residential Septage | Feedstock profile listing assumed feedstock characteristics of Residential Sewage
| PortableT Septage | Feedstock profile listing assumed feedstock characteristics of PortableT Septage
| Bath WAS | Feedstock profile listing assumed feedstock characteristics of Bath WAS
| Bath Primary Sludge | Feedstock profile listing assumed feedstock characteristics of Bath Primary Sludge
| Slaughterhouse Waste | Feedstock profile listing assumed feedstock characteristics of Slaughterhouse Waste
| Winery Waste | Feedstock profile listing assumed feedstock characteristics of Winery Waste
| Cheese Waste | Feedstock profile listing assumed feedstock characteristics of Cheese Waste
| HSOW Biogas | Documents biogas production rates for High Strength Organic Waste feedstocks
| References | Reference list
| Conversion Factors | (Hidden) Repository of conversion factors used throughout the workbook
Contacts:
Ben Morelli (ERG), ben.morelli@erg.com, 781-674-7223
Sarah Cashman (ERG), sarah.cashman@erg.com, 781-674-7233

## AD Scenarios
Anaerobic Digester Sensitivity Scenarios and Parameter Values
Sheet Description: Lists and describes the feedstock and operational parameter scenarios used in the anaerobic digester sensitivity analysis.
Table 1. Feedstock Scenarios (gal/day)
| Waste Type | Base | Medium | High | [5 empty] | Feedstock Scenario Description: Feedstock scenarios are developed using low to medium-high volatile solids loading rates, which are calculated based on the anaerobic digester size as determined by GHD Engineering. The digesters are 45 feet in diameter with a 23.5 foot side-wall depth. Quantities of primary, waste activated, septic tank, and portable toilet waste hold constant across the scenarios with the quantity of accepted industrial waste varying to achieve the loadings shown in the table at left. Tchobanogous et al. (2014) suggest that the acceptable range of anaerobic digester loading rates is between 100 and 300 lb VS/1000 ft3/day. The original GHD anaerobic digester calculations assumed a moisuture content in dewatered sludge of 4% as opposed to the 6% assumption that is now being used, which accounts for the difference in the calculated loading rate for the base scenario, which is similar to their original anaerobic digester scenario.
| Primary Sludge | 17654.2014 | 17654.2014 | 17654.2014
| Waste Activated Sludge | 75556.9523 | 75556.9523 | 75556.9523
| Septic Waste | 14000 | 14000 | 14000
| Slaughterhouse Waste | 0 | 1000 | 4000
| Cheese Waste | 0 | 2000 | 3000
| Winery Waste, Vinasse | 0 | 1000 | 1000
| Portable Toilet Waste | 2000 | 2000 | 2000
| Loading (lb VS/1000 ft3/day) | 130 | 158 | 205
Table 2. Anaerobic Digestion Operational Parameters
| Parameter Name |  | Low Yield |  | Base Yield |  | High Yield |  | Units | Operational Parameter Discussion: Given the novel combination of industrial waste products included in this study the precise determination of anaerobic digester operational parameters is not possible within the scope of this research. Instead a range of scenarios have been developed that consider the expected range of operational parameters based on indications from past projects and the literature. The base scenario is designed as a conservative scenario that adheres to conservative, conventional estimates regarding biogas heat content and yield associated with anaerobic digester operation. The medium and high yield scenarios correspond to increasingly optimistic, yet justifiable, assumptions associated with the parameters listed to the left. The high yield scenario will generally produce the most biogas and avoided heat and electricity production. For a more detailed discussion of factors affecting these parameters, please refer to the project report.
|  |  | Value | Reference | Value | Reference | Value | Reference
| Percent Volatile Solids Reduction |  | 45 | a | 60 | a | 65 | a | %
| Biogas Yield | Base Feedstock | 12 | calculated | 15 | calculated | 34.6555 | calculated | ft3/lb VS destroyed
|  | Medium Feedstock | 12.7806 | calculated | 16.7335 | calculated | 29.9933 | calculated | ft3/lb VS destroyed
|  | High Feedstock | 14.2056 | calculated | 19.2087 | calculated | 29.1107 | calculated | ft3/lb VS destroyed
| Methane Content of Biogas |  | 60 | b | 65 | b | 70 | b | % by volume (dry)
| Biogas Heat Content (MJ/ft3) |  | 0.54865 | b | 0.59086 | b | 0.61196 | b | MJ/ft3
| Electrical Efficiency |  | 30 | b | 36.3 | c | 42 | b | %
| Thermal Efficiency |  | 41 | b | 50.8 | c | 43 | b | %
| Reactor Heat Loss |  | Northern US | d | Northern US | d | Northern US | d | n.a.e
Notes & References:
a-Appleton and Rauch Williams 2017
b-Wiser et al. 2010
c-GHD 2016
d-Harris et al. 1982
e-n.a. = not applicable
Table 3. Biogas Yield Values (ft3 biogas per lb VS destroyed)
| Feedstock | Low Yield |  | Base Yield |  | High Yield
|  | Value | Reference | Value | Reference | Value | Reference
| Primary Sludge | 12 | c,a | 15 | a | 43.5385 | b
| Waste Activated Sludge | 12 | c,a | 15 | a | 18 | calculated
| Slaughterhouse Waste | 16.9677 | c,d,e | 23.8609 | c,d,e | 29.3672 | c,d,e
| Cheese Waste | 11.0733 | c,g | 14.889 | c,g | 15.9364 | c,g
| Winery Waste, Vinasse | 9.9671 | f | 14.0162 | f | 17.2507 | f
Notes & References:
a–Harris et al. 1982
b–GHD 2016,
c–20% reduction in biogas yield due to ammonia inhibition (IEA 2009)
d–Braun and Wellinger 2003
e–Luste and Luostarinen 2010
f–Belhadj et al. 2013
g-Rico et al. 2014
Table 4. Typical Biogas Composition
| Biogas Component | Expected Rangea
| Methane (CH4) | 60-70%
| Carbon Dioxide (CO2) | 30-40%
| Water Vapor (H2O) | <5%
Nitrogen (N2)
Hydrogen (H2)
Hydrogen Sulfide (H2S)
Notes & References:
a–Wiser et al. 2010, dry basis, by volume
Notes on AD operation:
| 1 | VS destruction usually 40-60% (Harris et al. 1982, 2.19-45)
| 2 | The standard CAPDET VS destruction assumption for municipal wastewater is 50% (Harris et al. 1982)
| 3 | standard CAPDET biogas yield is 15 ft3/pound of VS destroyed
| 4 | GHD LCCA assumes a methane content of 65%
| 5 | Pilot tests for ClearCove sludge indicate methane yield of 28.3 ft3 methane/lb of VS destroyed (assume 65% CH4)
| 6 | slaughter house waste is crushed to a particle size of 12 mm and pasteurized at 70 degrees C for 60 minutes.
| 7 | methane yield could be increased by 20% when ammonia was removed (IEA 2009). Used as basis of 20% reduction in biogas yield for low scenario.
| 8 | methane content ranged from 53% to 65%, but not all of this production was during a stable phase of operation (Jasko et al. 2011)
| 9 | typically, digester gas contains 55 to 70% methane, 30-40 percent CO2, N2, H2, H2S, and water vapor (Tchobanoglous et al. 2014)

## AD Design Info
AD Feedstock Calculator | [8 empty] | Anaerobic Digestion Feedstock Additions
This sheet allows the user to select from 3 feedstock and AD operational performance scenarios or to enter their own custom parameters for calculation of the resulting AD LCI values.
Set Prior to each run
|  | Changing value will alter results. Assumed to be standard across scenarios. | [6 empty] | Feedstock Values Currently in Use | [5 empty] | Feedstock Scenario Values (gal/day)
|  | Calculated value. Don't change. | [6 empty] | Source | Volume | Units | Source | Mass | Units | Waste Type | Base | Medium | High | Custom
|  | Reference value only, not used in calculations. | [6 empty] | Primary Sludge | 17654 | gal/day | calculated | 148390.3975 | lb/day | Primary Sludge | 17654 | 17654.2014 | 17654.2014
[9 empty] | Waste Activated Sludge | 75556.9523 | gal/day | calculated | 631340.892 | lb/day | Waste Activated Sludge | 75556.9523 | 75556.9523 | 75556.9523
| User Defined Values - SELECT FEEDSTOCK AND AD OPERATIONAL PERFORMANCE SCENARIO HERE | [7 empty] | Septic Waste | 14000 | gal/day | GHD LCCA | 116881.7166 | lb/day | Septic Waste | 14000 | 14000 | 14000
| Set Feedstock Scenario | Base | [6 empty] | Slaughterhouse Waste | 0 | gal/day |  | 0 | lb/day | Slaughterhouse Waste | 0 | 1000 | 4000
| Set Anaerobic Digester Scenario | Low | [6 empty] | Cheese Waste | 0 | gal/day |  | 0 | lb/day | Cheese Waste | 0 | 2000 | 3000
[9 empty] | Winery Waste, Vinasse | 0 | gal/day |  | 0 | lb/day | Winery Waste, Vinasse | 0 | 1000 | 1000
| Parameter | Value | Units | [5 empty] | Portable Toilet Waste | 2000 | gal/day |  | 16707.4832 | lb/day | Portable Toilet Waste | 2000 | 2000 | 2000
| Wastewater Flow | 1 | MGD | [5 empty] | Total | 109210.9523 | gal/day |  | 913320.4892 | lb/day | Loading (lb VS/1000 ft3/day) | 132.1662 | 157.6354 | 205.3823 | -
[9 empty] | *Values prior to dewatering | [5 empty] | Trucking Volume | 16000 | 20000 | 24000 | 0
Assumed Values
| VSS of influent water | 77.5% | percent of TSS | Tchobanoglous et al. 2014 pg. 221. |  |  |  |  | Mass of Sludge to GBT | 825928.4427 | lb/day |  |  |  | Other Custom Parmaters
[9 empty] | *Septic and portable toilet waste are processes with incoming wastewater in chemically enhanced primary clarification. Mass of water removed during primary clarification is removed in this calculation. | [5 empty] | Percent Volatile Solids Reduction | 50 | % (not as decimel)
| Chemically Enhanced Primary Clarification Performance | [13 empty] | CHP Electrical Efficiency | 36% | % as decimel
| Parameter | Value | Source | [11 empty] | CHP Thermal Efficiency | 54% | % as decimel
| BOD Removal | 65% | GHD 2016 | [5 empty] | Sludge Specifications To Gravity Belt Thickener | [5 empty] | # of Primary Anaerobic Digesters | 1 | count
| TSS Removal | 73.5% | GHD 2016 | [5 empty] | Parameter | Value | Unit |  |  |  | Biogas Yield | 15 | ft3/lb VS destroyed
| VSS Removal | 70% | GHD 2016 | [5 empty] | Solids Content, raw, unthickened sludge | 0.7474 | % w/w |  |  |  | Kraft Waste VS % | 65% | % as decimel
| TN Removal | 28% | GHD 2016 | [5 empty] | Total Solids Loading | 6173.0418 | lb/day
| TP Removal | 70% | GHD 2016 | [5 empty] | Specific Gravity sludge* | 1.0024
[9 empty] | Total Volatile Solids | 50.97%
| Wastewater Loading | includes trucked septage waste |  |  |  | alternatve values for reference |  |  | * Links to values from industrial waste profiles
| Parameter | Value | Unit | Calculated Value | Units | Value | Units | Source
| Flow | 1 | MGD | [5 empty] | Sludge Specifications Straight to Blending
| BOD | 323 | mg/L | 2686.068 | lbs/day | 2170 | lbs/day | CRA 2015, pg 18 | Parameter | Value | Unit
| TSS | 437 | mg/L | 3849.4025 | lbs/day | 3460 | lbs/day | CRA 2015, pg 18 | Solids Content, raw, unthickened sludge | 0 | % w/w
| VSS | 338.675 | mg/L | 2931.2536 | lbs/day |  |  |  | Total Solids Loading | 0 | lb/day
| TKN | 56 | mg/L | 465.696 | lbs/day | 455 | lbs/day | CRA 2015, pg 18 | Specific Gravity* | 0
| NH3 | 32.3 | mg/L | 268.6068 | lbs/day | 246 | lbs/day | CRA 2015, pg 18 | Total Volatile Solids | 0%
| TP | 8 | mg/L | 66.528 | lbs/day | 67 | lbs/day | CRA 2015, pg 18 | * Links to values from industrial waste profiles
| BOD, primary sludge | 1745.9442 | lb/day
| BOD, WAS, solids | 1003.1193 | lb/day | [5 empty] | Biogas Yield
| bCOD, primary sludge | 2793.5107 | lb/day | [5 empty] | Low | Base | High
| bCOD, WAS, solids | 1604.9909 | lb/day | [5 empty] | 12 | 15 | 34.6555
| TKN, primary sludge | 70.7328 | lb/day | [5 empty] | * Columns refer to AD Scenario
| TKN, WAS | 127.0618 | lb/day
| TP, primary sludge | 19.7552 | lb/day
| TP, WAS | 80.2557 | lb/day
| TSS, primary sludge, solids | 2829.3108 | lb/day | 242.0114 | gal/day | 2200 | lbs/day | CRA 2015, pg 22
| TSS, Waste activated sludge, solids | 3343.731 | lb/day | 320.3351 | gal/day | 2600 | lbs/day | CRA 2015, pg 22
| VSS, primary sludge, solids | 2051.8775 | lb/day |  |  | 1500 | lbs/day | CRA 2015, pg 22
| VSS, Waste activated sludge, solids | 1094.3347 | lb/day |  |  | 800 | lbs/day | CRA 2015, pg 22
| COD, primary sludge, solids | 2913.666 | lb/day
| COD, waste activated sludge, solids | 1553.9552 | lb/day
AD design flows - From GHD Report (for reference only)
| Parameter | Value | Unit | Source
| Flow | 21000 | gal/day | CRA 2015
| Total solids concentration | 4 | % | CRA 2015
| Total solids, mass | 7000 | lbs/day | CRA 2015
| Volatile solids | 55 | % | CRA 2015
| TVS mass loading | 3600 | lbs/day | CRA 2015
| biogass production | 18 | ft3/lb VSS destroyed | CRA 2015
Septage Waste
| Parameter | Value | Unit | Calculated Value | Units
| Influent Septage, Solids | 160.0642 | lb/day | 13.2279 | gal/day
| Influent Septage, TVS | 91.1314 | lb/day
| Influent Septage, BOD | 62.1563 | lb/day
| Influent Septage, COD | 168.2426 | lb/day
| Influent Septage, TKN | 12.034 | lb/day
| Influent Septage, TP | 1.6357 | lb/day
| Influent Septage, Water Content | 116721.6524 | lb/day | 13986.7721 | gallons per day
| Primary Sludge from Septage, Solids | 1.8 | % w/w
| Mass sludge from Septage as Primary | 6535.9536 | lb/day
| Mass solids in WAS | 139.0376 | lb/day
| WAS solids content | 0.5 | % w/w
| Mass sludge from Septage as WAS | 27807.5115 | lb/day
Slaughterhouse Waste (SHW)
| Parameter | Value | Unit | Calculated Value | Units
| Slaughterhouse Waste Solids | 0 | lb/day | 0 | gal/day
| TVS | 0 | lb/day
| COD in SHW | 0 | lb/day
| Water Content | 0 | lb/day | 0 | gal/day
Winery Waste, Vinasse
| Parameter | Value | Unit | Calculated Value | Units
| Winery Solids | 0 | lb/day | 0 | gal/day
| TVS | 0 | lb/day
| BOD in Vinasse | 0 | lb/day
| COD in Vinasse | 0 | lb/day
Cheese Waste, Whey
| Parameter | Value | Unit | Calculated Value | Units
| Whey Solids | 0 | lb/day | 0 | gal/day
| TVS | 0 | lb/day
| COD in Whey | 0 | lb/day
| Water Content | 0 | lb/day | 0 | gal/day
Portable Toilet Waste
| Parameter | Value | Unit | Calculated Value | Units
| Influent Portable Toilet Waste, Solids | 55.2463 | lb/day | 4.5601 | gal/day
| Influent Portable Toilet Waste, TVS | 23.7008 | lb/day
| Influent Portable Toilet Waste, BOD | 53.5773 | lb/day
| Influent Portable Toilet Waste, COD | 86.458 | lb/day
| Influent Portable Toilet Waste, TKN | 15.6392 | lb/day
| Influent Portable Toilet Waste, TP | 1.13 | lb/day
| Influent Portable Toilet Waste, Water Content | 16652.2368 | lb/day | 1995.4399 | gal/day
| Solids Content of Primary Sludge | 1.8 | % w/w
| Mass sludge from Septage as Primary | 2255.8922 | lb/day
| Mass solids in WAS | 47.989 | lb/day
| WAS solids content | 0.5 | % w/w
| Mass sludge from Septage as WAS | 9597.7959 | lb/day
Summary of Industrial Organic Wastes
| Feedstock | Total Solids (lb/day) | Volatile Solids (lb/day) | Percent of Total VS
| Primary Sludge | 2829.3108 | 2051.8775 | 65.22%
| Waste Activated Sludge | 3343.731 | 1094.3347 | 34.78%
| Slaughterhouse Waste | 0 | 0 | 0%
| Cheese Waste, Whey | 0 | 0 | 0%
| Winery Waste | 0 | 0 | 0%
| Totals | 6173.0418 | 3146.2122 | 100%
*Septage and Portable Toilet Waste are included within Primary and waste activated sludge.

## AD CAPDET
Anaerobic Digester Calculator
This worksheet deploys the CAPDETWorks Anaerobic Digester design equations (from Harris et al. 1982) in an excel workbook that allows dyamic calculation of AD performance based on influent feedstock quantities and quality
| AD design flows | [5 empty] | Conversions
| Description | Abbreviated Description | Value | Units | Source | Note | Description | Value | Unit (if not in description)
| m3 water treated per day |  | 3785 | m3/day | calculated |  | gal/ft3 | 7.4805
| m3 water treated per year |  | 1381675 | m3/yr | calculated |  | lb/gal water | 8.34
| Pre-GBT Sludge Mass |  | 825928.4427 | lb/day | calculated | excludes industrial wastes which skip the GBT | Biogas Heat Content1 | 21 | MJ/m3
| Solids, to thickener |  | 6173.0418 | lbs/day | calculated on previous sheet | based on scenario | BTU/MJ | 947.7778
| % solids in influent sludge (prior to Gravity Belt Thickener (GBT)) | %S | 0.7474 | % | calculated |  | 1 Bond 2011
| Pre-GBT Specific Gravity |  | 1.0024 |  | calculated
| Solids Content reached via GBT | Ps | 6 | % | Assumed | assume that GBT hits 5-6 percent solids regardless of influent moisture/solids content | GHD AD Design Specs to the Right.
| Post-GBT Sludge Mass | SM | 102884.0307 | lb/day | calculated
| Specific Gravity (post GBT) | S.G. | 1.0191 |  | calculated | Value for nutrient removal project was 1.05
| Post-GBT Sludge Flow | SF | 12097.248 | gal/day | calculated
| Total Volatile Solids, Post GBT | TVS | 50.967 | % | calculated
| Skip GBT, Solids Content |  | 0 | % | calculated
| Skig GBT, Specific Gravity |  | 0 |  | calculated
| Skip GBT, Sludge Flow |  | 0 | gal/day | calculated
| Skip GBT, Sludge Mass |  | 0 | lb/day | calculated
| Skip GBT, Volatile Solids |  | 0 | % | calculated
| Combined Solids Content |  | 6 | % w/w | calculated
| Combined Mass, sludge |  | 102884.0307 | lb/day | calculated
| Combined Mass, Solids |  | 6173.0418 | lb/day | calculated | assume no solids loss in GBT
| Combined Volume |  | 12097.248 | gal/day | calculated
| Combined Specfic Gravity |  | 1.0191 | w/w | calculated
| Combined Volatile Solids |  | 50.967 | % | calculated
| Reference Percent Volatile Solids Reduction | PVRref | 56.0003 | % | calculated from CAPDET, needs adjusted downwards. | calc method from Tchobanoglous, equation also used in CAPDET method.
| Scenario Percent Volatile Solids Reduction | PVRf | 45 | % | scenario value (assumed) | CAPDET Standard is 50%
| Percent Solids in Digested Sludge | PSD | 7 | % | CAPDET | CAPDET assumes 1% increase
| Specific Gravity of Digested Solids |  | 1.0223 |  | calculated
| Biogas Heat Content | Hb | 520 | BTU/ft3 | scenario value (calculated) | 600 BTU/ft3 is CAPDET default
| Digester Temperature | Td | 95 | °F | user defined
| Incoming Sludge Temperature | Ts | 65 | °F | user defined
| biogas production per lb VS destroyed | Bp | 12 | ft3/lb VS destroyed | scenario value (calculated)
| VSS Loading Rate (primary digester) |  | 129.7265 | lb VS/1000 ft3/day | calculated | Acceptable Range 100-300: Target 200.
| VSS Loading Rate (primary digester) |  | 1.6662 | kg VS/m3/day | calculated
| Calculate Sludge Production: |  |  |  |  | Screenshots from CAPDETWorks Technical Reference
| Description | Abbreviated Description | Value | Units
| Solids produced, Total | Sp | 6169.2354 | lb/day
| Volatile Solids | Svs | 3144.2721 | lb/day
Calculate Sludge Volume:
| Volume of raw sludge to digester | Vf | 1616.8437 | ft3/day
|  |  | 45.7839 | m3/day
Calculate Digester Time:
| Time in Digester1 | td | 15 | days
1 suggested by Tchobanoglous et al. 2014, CRA 2015 value is 15
Standard Anaerobic Digester Tank Volumes (from CAPDET)
| Calculate Quantity & Volume of Digested Sludge | [5 empty] | Diameter (ft) | Side Water Depth (ft) | Volume (ft3)
| Description | Abbreviated Description | Value | Units |  |  | 25 | 20 | 10330
| Number of Primary Digesters |  | 1 | count |  |  | 30 | 21 | 15727
| Volume of Primary | Vp | 24252.6559 | ft3 |  |  | 35 | 21.5 | 22087
| Volume of Secondary | Vs | 24252.6559 | ft3 |  |  | 40 | 22.5 | 30367
|  |  | 181409.8662 | gal |  |  | 45 | 23.5 | 40355
[7 empty] | 50 | 24.5 | 52193
| Calculate Digester Volume, Size & Heat Requirement | [5 empty] | 55 | 25 | 64836
| Description | Abbreviated Description | Value | Units |  |  | 60 | 26 | 80577
| Digester Diameter |  | 45 | ft |  |  | 65 | 27 | 98575
| Sludge Heating Requirement | Qs | 128525.7374 | BTU/hr |  |  | 70 | 28 | 118980
| Heat loss through digester walls | Ql | 292204.5908 | BTU/hr |  |  | 75 | 28.5 | 139704
| Total Heat loss | Qt | 420730.3282 | BTU/hr |  |  | 80 | 29.5 | 148493
| Annual Natural Gas Requirement | = | 3588.7027 | MCF (1,000 ft3) |  |  | 85 | 30 | 190317
| Annual Biogas Heat Requirement | = | 7087.6878 | MCF (1,000 ft3) |  |  | 90 | 31.5 | 224233
| % of total biogas required for heating | = | 114.4% |  |  |  | 95 | 32 | 254810
[7 empty] | 100 | 33 | 291882
| Biogas Production | [5 empty] | 110 | 35 | 376141
| Description | Abbreviated Description | Value | Units
| Yearly Gas Production | YGP | 6197360.3794 | cuft/year
| Daily Gas Production | DGP | 16979.0695 | cuft/day
| Hourly Gas Production | HGP | 707.4612 | cuft/hr
| Gas Production per minute | MGP | 11.791 | cuft/min
| Biogas Production |  | 0.12701 | m3/m3
Energy Production Potential:
| Description | Abbreviated Description | Value | Units
| Daily Energy Content of Biogas | DHP | 8829116.157 | BTU
|  | DHP | 9315.5974 | MJ
|  | DHP | 2587.6659 | kWh
| Description | Value | Units
| Electrical Efficiency | 30% | from LCC
| Thermal Efficiency | 41% | from LCC
| Description | Value | Units
| Daily Electricity production | 776.2998 | kWh
| Daily Heat Production | 3819.3949 | MJ
| Avoided Electricity | 0.2051 | kwh/m3
| Description | Value | Units
| Annual Average Building Heat Requirement* | 1.065 | MJ/m3
| Annual Average Anaerobic Digester Heat Requirement | 2.8096 | MJ/m3
| Avoided Heat Production | 1.0091 | MJ/m3
| Total Heat Production | 1.0091 | MJ/m3
| Wasted Heat | 0 | MJ/m3
| Avoided Natural Gas, Total | 0.026416 | m3/m3
| Required Natural Gas, Total | 0.075013 | m3/m3
| Total Natural Gas Equivalent | 0.026416
* Assumes 50% increase over current historic building heat requirements to account for new control and service buildings.
Calculate Sludge Flow Out of Digester
| Description | Abbreviated Description | Value | Units
| Non-volatile solids, remaining in digestate |  | 3024.9633 | lb/day
| Volatile Solids, remaining in digestate |  | 1729.3497 | lb/day
| Quantity of Solids, remaining in digestate | SD | 4754.3129 | lb/day
| Solids Out of Digester |  | 2.3772 | short ton/day
| VS content of digested sludge (% TS) |  | 36.3743 | %
| Sludge Flow Out | SFO | 7965.9945 | gal/day
| Volume of digested solids |  | 559.0188 | gal/day
| Mass of Digested Sludge |  | 30807.4662 | kg/day
| Solids Concentration, out of Belt Filter Press |  | 20%
| Mass of Dewatered (hauled) sludge |  | 10782.6132 | kg/day
| Mass of Solid |  | 2156.5226 | kg/day
| Mass of Water |  | 8626.0905 | kg/day
| Volume of Water |  | 8.6263 | m3
| Volume of Solids |  | 2.1161 | m3
| Density of Hauled Digested Sludge |  | 1003.7372 | kg/m3
|  | Dewatered Sludge Mass | 10.7826 | tonne/day
|  | Dewatered Sludge Mass | 3935.6538 | tonne/year
| Description | Abbreviated Description | Value | Units
| Distance Hauled, to Compost Facility |  | 0.8 | km
| Ton-km of hauling |  | 0.002279 | tkm/m3

## Composting & Land Application
Compost Calculator
| Choose Compost Emission Scenario | Base | Select from dropdown
| Parameter | Value | Unit | Note
| Current Scenario Selection | Base-Low
| Incoming Sludge Quantity | 3935.6538 | metric ton/yr | linked
| Incoming Sludge Volume | 3921.0001 | m3/year
| Biosolids Incoming Moisture Content | 80 | % | Assumed value for sludge exiting the BFP
| Biosolids Incoming Solids Content | 20 | %
| Incoming Dry Matter | 787.1308 | metric ton/yr
| Incoming Carbon | 56.52% | dry basis | Based on C:N ratio of Maulini-Dran et al. 2013
| Incoming Nitrogen | 4.45% | dry basis | Average of Maulini-Duran et al. 2013 and Richard 2014
| Incoming Carbon | 444.847 | metric ton/yr
| Incoming Nitrogen | 35.0273 | metric ton/yr
| Incoming C:N | 12.7 | :1 | Maulini-Duran et al. 2013
|  | Carbon Content | Nitrogen Content
| Target C:N Ratio | 30 | :1 | Typical Range is 25:1 to 35:1
*Will only accept valus within the typical range
| Target Moisture Content | 55% | w/w | Target Moisture is in the range of 50-60%. 60% is ideal (Milczarek et al. 2013). Lower moisture can help prevent N2O emissions (Brown et al. 2009).
|  | To enter custom feedstock values scroll to the right--------->----------> |  | Feedstock Characteristics
| Feedstock | Quantity (metric ton/yr) | Percent of Total Compost Mixture (%) | Percent of Amendment | %H201 | C (% dry weight)1 | N (% dry weight)1 | C:N1 | Density (m3/kg)1,2,3 | Note
| Leaves Loose, Dry | 2500 | 38.76% | 99.4% | 15% | 48.6% | 0.9% | 54 | 0.0025795
| Grass, Loose | 0 | 0% | 0% | 82% | 57.8% | 3.4% | 17 | 0.0013959
| Newsprint | 15 | 0.2325% | 0.5964% | 5.5% | 62.5% | 0.1% | 625 | 0.0023529
| Leaves, Fresh | 0 | 0% | 0% | 38% | 48.6% | 0.9% | 54 | 0.0016951
| Food Waste | 0 | 0% | 0% | 87% | 39% | 3.25% | 12 | 0.0011542
| Chipped Wood | 0 | 0% | 0% | 40% | 57.69% | 0.09% | 641 | 0.0011152 | pine tree chips
| Total | 2515
| Amendment (Dry) | 2139.175
Sources: 1 Richard 2014 2 CWMI 1990, 3 Harris and Phillips 1986
Composting Combinations that Work (Metric Ton/year)
| Parameter | Value | Unit |  |  | Custom | Base-Low | Base-Base | Base-High | Medium-Low | Medium-Base | Medium-High | High-Low | High-Base | High-High
| Nitrogen Content, Leaves Loose, Dry | 19.125 | metric ton/yr |  |  |  | 2500 | 2250 | 2100 | 3400 | 3100 | 3000 | 4700 | 4300 | 4000
| Nitrogen Content, Grass, Loose | 0 | metric ton/yr |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nitrogen Content, Newsprint | 0.014175 | metric ton/yr |  |  |  | 15 | 15 | 10 | 25 | 25 | 20 | 35 | 35 | 25
| Nitrogen Content, Leaves, Fresh | 0 | metric ton/yr |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nitrogen Content, Food Waste | 0 | metric ton/yr |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nitrogen Content, Chipped Wood | 0 | metric ton/yr |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Incoming N | 54.1665 | metric ton/yr |  |  | *copy and paste into green cells at left to generate these results
| N, Percent of Incoming Dry Matter | 1.851% | dry basis
| Carbon Content, Leaves Loose, Dry | 1032.75 | metric ton/yr
| Carbon Content, Grass, Loose | 0 | metric ton/yr
| Carbon Content, Newsprint | 8.8594 | metric ton/yr
| Carbon Content, Leaves, Fresh | 0 | metric ton/yr
| Carbon Content, Food Waste | 0 | metric ton/yr
| Carbon Content, Chipped Wood | 0 | metric ton/yr
| Total Incoming C | 1486.4563 | metric ton/yr
| C, Percent of Incoming Dry Matter | 50.8% | dry basis
| Parameter | Value | Units | Reference Value
| Combined C:N Ratio | 30.1299 |  | 30.1299
| Combine Moisture Content | 54.6355 | % | 54.6355
| Combined Volume | 10404.9574 | m3/year of material
| Water Required (to reach 60% Moisture) | 52.2479 | metric tons/year
| Total Incoming Mass | 6450.6538 | metric tons/year
| Incoming Dry Matter | 2926.3058 | metric tons/year
| Incoming Carbon | 1486.4563 | metric tons/year
| Incoming Nitrogen* | 54.1665 | metric tons/year
| Carbon Content | 50.8% | of dry matter
| Nitrogen Content | 1.851% | of dry matter
| Incoming Water Quantity | 3524.348 | metric tons/year
| Volume of Water Required | 52.2495 | m3
| Percent of Annual Wastewater | 0.003782%
*Assumes only nitrogen losses during composting are associated with emissions of N2O and NH3.
| Daily material grinding requirement | 6.8904 | tons/day
*biosolids do not need grinding.
| Total incoming material | 17.673 | tons/day
| Parameter | Value | Units | Source
| Assumed Mass Loss | 52 | % | Tiquia et al. 2002, Fukumoto et al. 2003
*Range of 47-57% for turned windrows (Tiquia et al. 2002)
Select Amendment Scenario (include/exclude)
| Include Amendment in LCI calculations? | Yes
* Allows user to select whether or not to quantify the contribution of composting amendment to calculated LCI values. For purposes of assessing only biosolids impacts it is reasonable to assume that disposal (composting) LCI information should be allocated to the amendment itself given that this material is often composted regardless of biosolids management choices. However, when assessing total facility impacts, both amendment and biosolids must be considered.
Nutrient Content Calculations
| Parameter | Value | Unit | Note:
| Assumed Final Moisture Content | 45 | % total weight | Hellmann et al. 1997 shows a moisture loss of ~10%
| Mass Water Lost During Composting | 2131.0068 | metric tons
| % of Incoming Mass Lost as H2O | 33.04% | of total incoming mass
| % of Incoming Mass Lost as N | 0.1735% | of total incoming mass
| % of Incoming Mass Lost as C | 18.79% | of total incoming mass
| Mass of C Lost | 1212.1418 | metric tons
| Percent of Incoming C Lost | 81.55% | of initial Carbon mass | calculated close to 80-85% value reported by Hellebrand 1998
| Final Mass to Land Application | 8.4831 | tons/day
| Final Mass to Land Application | 3096.3138 | tons/year
| Mass of Solids to Land Application | 1702.9726 | tons/year
| Mass of Nitrogen Lost during composting | 5.0769 | tons/year
| Nitrogen Content | 49.0896 | tons/year
| Phosphorus Content | 8.5149 | tons/year
| Potassium Content | 3.4059 | tons/year
*Simplified mass balance considering only Carbon, Water, and Nitrogen
Windrow Compost LCI Calculations
| Parameter | Value | Units | Source/Note:
| Compost Haul | 0.8 | km | assumption |  |  | LCI Input Values
| Added material | 1.8203 | kg/m3 | calculated |  |  | Parameter | Value | Unit | Source:
| Mass of Compost to Land Application | 2.241 | kg/m3 | calculated |  |  | Shredding Diesel Use | 3.65 | L/tonne of feedstock | ROU 2006, Table 5.3
| Biosolids Hauling, incoming to composting | 0.0022788 | tkm/m3 | calculated |  |  | Compost Turning Diesel Use | 0.58 | L/tonne of feedstock | ROU 2006, Table 5.3
| Avoided Water | 3.7816e-05 | m3 H2O/m3 | calculated |  |  | Screening Diesel Use | 0.79 | L/tonne of feedstock | ROU 2006, Table 5.3
[7 empty] | Total Diesel Use | 5.02 | L/tonne of feedstock | ROU 2006, Table 5.3
| Windrow Compost LCI Calculations | [5 empty] | Electricity Use | 0.13 | kWh/tonne of feedstock | ROU 2006, Table 5.3
| Electricity Consumption (Shredding, Turning, Screening) | 0.00060693 | kWh/m3 | ROU 2006 |  |  | N2O emissions during composting | 0.5% | % incoming N | Hellebrand 1998
| Diesel Consumption (Shredding, Turning, Screening) | 0.023437 | L/m3 | ROU 2006 |  |  | NH3 emissions during composting | 1.2% | % incoming N | Hellebrand 1998
| N2O | 0.0016838 | kg (as N2O) | see Compost Research Tab of Bath LCI_Upgraded |  |  | CO2 emissions during composting | 81% | % incoming C | Hellebrand 1998
| NH3 | 0.0032561 | kg (as NH3) | see Compost Research Tab of Bath LCI_Upgraded |  |  | CH4 emissions during composting | 1.7% | % incoming C | Hellebrand 1998
| CO2 | 3.1952 | kg (as CO2) | see Compost Research Tab of Bath LCI_Upgraded |  |  | CO emissions during composting | 0.0004 | % incoming C | Hellebrand 1998
| CH4 | 0.011867 | kg (as CH4) | see Compost Research Tab of Bath LCI_Upgraded
| CO | 0.0010141 | kg (as CO) | see Compost Research Tab of Bath LCI_Upgraded
| NMVOC | 0.00019052 | kg NMVOC | see Compost Research Tab of Bath LCI_Upgraded |  |  | Fertilizer Application Rate
[7 empty] | Parameter | Value | Unit | Note
| Aerated Static Pile Compost LCI Calculations | [5 empty] | Nitrogen application rate | 50.3179 | kg N/acre | Fertilizer application rate determined on the basis of national fertilization rates. It is assumed that none of the major nutrients N/P/K can be applied at a rate that is greater than the national average. Based on the ratio of nutrients in the finished compost Phosphorus is the nutrient that limits its application and this value is set to 12.4 kg P2O5 per acre, which is the national average. Corresponding additions of N and K are calculated and emission estimates are determined using these input values. The annual quantity of wastewater allocated the avoided fertilizer benefits and emission impacts is calculated by applying the same percentage to annual wastewater treated as is determined by dividing this nutrient application by total annual nutrient content of composted biosolids.
| Electricity Consumption (Shredding, Turning, Screening) | 0.19061 | kWh/m3 | BEAM, CCME 2009 |  |  | P application rate | 15.748 | kg P2O5/acre
| Diesel Consumption (Shredding, Turning, Screening) | 0.011672 | L/m3 | BEAM, CCME 2009 |  |  | K application rate | 4.2056 | kg K2O/acre
| N2O | 0.0016838 | kg (as N2O) | BEAM, CCME 2009 |  |  | Cubic Meters of Wastewater treated for this quantity of nutrients | 1416.2472 | m3
| NH3 | 0.00016281 | kg (as NH3) | BEAM, CCME 2009 |  |  | Application Rate | 15.8542 | tons/acre
| CH4 | 0 | kg (as CH4) | BEAM, CCME 2009 |  |  | *10-20 tons per acre is a reasonable range
| CO | 0.0010141 | kg (as CO) | BEAM, CCME 2009
| NMVOC | 9.5258e-06 | kg NMVOC | BEAM, CCME 2009 |  |  | Agricultural Emissions
| Land Application LCI Calculations | [5 empty] | Emission Factor | Value | Unit | Source/Note
| Parameter | Value | Units | Source/Note: |  |  | Fertilizer replacement value | 73% | of applied nutrient | Smith (originally intended for Nitrogen)
| Distance to Land Application Site | 25 | km | assumption |  |  | Nitrous Oxide - 1 | 1.17% | of N applied | Myhre et al. 2013, from CH4 and N2O emissions from waste water handling
| Transit to Land Application Site | 0.056031 | tkm/m3 | calculated |  |  | Ammonia - 1 | 16.53% | of N applied | Potter et al. 2006, Wang 2014
| Avoided Urea | 0.025936 | kg (as N)/m3 | calculated |  |  | NO3 - 1 | 10.52% | of N applied | Potter et al. 2006, Wang 2014
| Avoided Rock Phosphate | 0.010309 | kg (as P2O5)/m3 | calculated |  |  | Nitrous Oxide - 2 | 1.0099 | kg N2O | Wang 2014, calculated for N application to corn fields China
| Avoided Potash | 0.0021678 | kg (as K2O)/m3 | calculated |  |  | Ammonia - 2 | 13.6549 | kg NH3 | Wang 2014, calculated for N application to corn fields China
| Handling and spreading | 0.0023754 | L/m3 | ROU 2006 |  |  | NO3 - 2 | 31.6967 | kg NO3 | Wang 2014, calculated for N application to corn fields China
| Nitrous Oxide -1 | 0.00017637 | kg (as N2O)/m3 | calculated |  |  | Phosphorus, surface water, on sediment | 0.69271 | kg as P | Potter et al. 2006
| Ammonia - 1 | 0.0019258 | kg (as NH3)/m3 | Potter et al. 2006, Wang 2014 |  |  | Phosphorus, surface water, soluble | 0.21991 | kg as P | Potter et al. 2006
| NO3 - 1 | 0.0044703 | kg NO3/m3 | Potter et al. 2006, Wang 2015 |  |  | Phosphate, groundwater, soluble | 0.021991 | kg as P | Potter et al. 2006
| Phosphorus, surface water, on sediment | 0.00013206 | kg P/m3 | calculated, Potter et al. 2006 |  |  | Phosphorus, windborne, on sediment | 0.16493 | kg as P | Potter et al. 2006
| Phosphorus, surface water, soluble | 4.1924e-05 | kg P/m3 | calculated, Potter et al. 2006 |  |  | Percent of N lost as N2O | 1.277% | % of applied N | Wang 2014, calculated for N application to corn fields China
| Phosphate, groundwater, soluble | 4.1924e-06 | kg P/m3 | calculated, Potter et al. 2006 |  |  | Percent of N lost as NH3 | 22.35% | % of applied N | Wang 2014, calculated for N application to corn fields China
| Phosphorus, windborne, on sediment | 3.1443e-05 | kg P/m3 | calculated, Potter et al. 2006 |  |  | Percent of N lost as NO3 | 14.22% | % of applied N | Wang 2014, calculated for N application to corn fields China
| Carbon Credit from Compost Land Application | -0.52949 | kg CO2 eq sequestered/m3 | calculated |  |  | Percent of applied nitrogen lost to cumulative N emissions | 37.85% | % of applied N | used these relative losses with the NRCS calculated N loss rate of 28%
| Nitrous Oxide -2 | 0.00071309 | kg (as N2O)/m3 | calculated, Wang 2014 |  |  | From biosolids/compost applications | 0.25 | (Mg CO2/dry Mg-biosolids) | BEAM default
| Ammonia - 2 | 0.0096416 | kg (as NH3)/m3 | calculated, Wang 2014 |  |  | Percent of Incoming C Sequestered | 0.14979 |  | calculated
| NO3 - 2 | 0.022381 | kg NO3/m3 | calculated, Wang 2014 |  |  | Percent of Land Applied C Sequestered | 0.81167 |  | calculated
Assumed Final Compost Physical Characteristics
| Parameter | Value | Unit |  |  |  | Aerated Static Pile - Composting Method
| Organic Matter | 55-75 | % dry matter |  |  |  | Fuel -Aerated Static Piles (ASP) | 2.5 | L/Mg feedstock- wet | Brown et al, JEQ 2008
| Total N | 2.8826 | % dry matter |  |  |  | Aeration electricity use ASP | 90 | kWh/dry Mg compost | 90 is the value in Brown et al, JEQ 2008 - the reference within the study is Steve Diddy personal communication - and this 180 is assuming that, on a dry weight basis, biosolids and wood feedstocks will be mixed 1 to 1
| Total P1 | 0.5 | % dry matter |  |  |  | Ammonia Reduction | 0.95 | Reduction | Williams 2009 | assumes open window as baseline for reduction
| Total K1 | 0.2 | % dry matter |  |  |  | VOC Reduction | 0.95 | Reduction | Williams 2009 | assumes open window as baseline for reduction
1 ROU 2006, Table 2.1 - composted soil conditioner

## Composting Emissions
Database of Composting Emissions
Values are calculated in the Bath LCI_Upgraded Workbook
| Emission Scenario | Feedstock-AD Scenario | Emission Species | Element | LCI Emission Factor | LCI Units | Value 2 | Units 2 | Loss of Incoming Element to GHGs | Units | Incoming Carbon Mass by feedstock and anaerobic digester scenario1
| Low | Base-Low | CH4 | C | 0.0015556 | kg CH4/m3 wastewater | 1.612 | ton C | 0.1074% | % of incoming C lost as CH4 | Feedstock Scenario | AD Scenario (Carbon to composting)
| Low | Medium-Low | CH4 | C | 0.0021396 | kg CH4/m3 wastewater | 2.2172 | ton C | 0.1072% | % of incoming C lost as CH4 |  | Low | Base | High
| Low | High-Low | CH4 | C | 0.0029718 | kg CH4/m3 wastewater | 3.0796 | ton C | 0.1072% | % of incoming C lost as CH4 | Base | 1501.1663 | 1368.4713 | 1274.1332
| Low | Base-Base | CH4 | C | 0.0014162 | kg CH4/m3 wastewater | 1.4675 | ton C | 0.1072% | % of incoming C lost as CH4 | Medium | 2067.6286 | 1896.1263 | 1804.291
| Low | Medium-Base | CH4 | C | 0.0019609 | kg CH4/m3 wastewater | 2.032 | ton C | 0.1072% | % of incoming C lost as CH4 | High | 2873.3609 | 2630.7316 | 2423.506
| Low | High-Base | CH4 | C | 0.0027205 | kg CH4/m3 wastewater | 2.8192 | ton C | 0.1072% | % of incoming C lost as CH4
| Low | Base-High | CH4 | C | 0.0013191 | kg CH4/m3 wastewater | 1.3669 | ton C | 0.1073% | % of incoming C lost as CH4 | Incoming Nitrogen Mass by feedstock and anaerobic digester scenario1
| Low | Medium-High | CH4 | C | 0.0018693 | kg CH4/m3 wastewater | 1.9371 | ton C | 0.1074% | % of incoming C lost as CH4 | Feedstock Scenario | AD Scenario (tons Nitrogen to composting)
| Low | High-High | CH4 | C | 0.002509 | kg CH4/m3 wastewater | 2.6 | ton C | 0.1073% | % of incoming C lost as CH4 |  | Low | Base | High
| Low | Base-Low | N2O | N | 0.00021817 | kg N2O/m3 wastewater | 0.19182 | ton N | 0.3467% | % of incoming N lost as N2O | Base | 55.3248 | 51.0957 | 47.627
| Low | Medium-Low | N2O | N | 0.00030008 | kg N2O/m3 wastewater | 0.26385 | ton N | 0.3423% | % of incoming N lost as N2O | Medium | 77.0827 | 71.0418 | 66.5263
| Low | High-Low | N2O | N | 0.0004168 | kg N2O/m3 wastewater | 0.36647 | ton N | 0.3402% | % of incoming N lost as N2O | High | 107.7297 | 98.5761 | 90.178
| Low | Base-Base | N2O | N | 0.00019862 | kg N2O/m3 wastewater | 0.17464 | ton N | 0.3418% | % of incoming N lost as N2O | 1 Values copied here from within this worksheet for the labeled scenario combination
| Low | Medium-Base | N2O | N | 0.00027502 | kg N2O/m3 wastewater | 0.24181 | ton N | 0.3404% | % of incoming N lost as N2O
| Low | High-Base | N2O | N | 0.00038155 | kg N2O/m3 wastewater | 0.33548 | ton N | 0.3403% | % of incoming N lost as N2O
| Low | Base-High | N2O | N | 0.000185 | kg N2O/m3 wastewater | 0.16266 | ton N | 0.3415% | % of incoming N lost as N2O
| Low | Medium-High | N2O | N | 0.00026217 | kg N2O/m3 wastewater | 0.23051 | ton N | 0.3465% | % of incoming N lost as N2O
| Low | High-High | N2O | N | 0.00035189 | kg N2O/m3 wastewater | 0.3094 | ton N | 0.3431% | % of incoming N lost as N2O
| Low | Base-Low | NH3 | N | 0.00058347 | kg NH3/m3 wastewater | 0.6639 | ton N | 1.2% | % of incoming N lost as NH3
| Low | Medium-Low | NH3 | N | 0.00081293 | kg NH3/m3 wastewater | 0.92499 | ton N | 1.2% | % of incoming N lost as NH3
| Low | High-Low | NH3 | N | 0.0011361 | kg NH3/m3 wastewater | 1.2928 | ton N | 1.2% | % of incoming N lost as NH3
| Low | Base-Base | NH3 | N | 0.00053887 | kg NH3/m3 wastewater | 0.61315 | ton N | 1.2% | % of incoming N lost as NH3
| Low | Medium-Base | NH3 | N | 0.00074922 | kg NH3/m3 wastewater | 0.8525 | ton N | 1.2% | % of incoming N lost as NH3
| Low | High-Base | NH3 | N | 0.0010396 | kg NH3/m3 wastewater | 1.1829 | ton N | 1.2% | % of incoming N lost as NH3
| Low | Base-High | NH3 | N | 0.00050228 | kg NH3/m3 wastewater | 0.57152 | ton N | 1.2% | % of incoming N lost as NH3
| Low | Medium-High | NH3 | N | 0.0007016 | kg NH3/m3 wastewater | 0.79831 | ton N | 1.2% | % of incoming N lost as NH3
| Low | High-High | NH3 | N | 0.00095104 | kg NH3/m3 wastewater | 1.0821 | ton N | 1.2% | % of incoming N lost as NH3
| Base | Base-Low | CH4 | C | 0.011867 | kg CH4/m3 wastewater | 12.2976 | ton C | 0.8192% | % of incoming C lost as CH4
| Base | Medium-Low | CH4 | C | 0.016352 | kg CH4/m3 wastewater | 16.9446 | ton C | 0.8195% | % of incoming C lost as CH4
| Base | High-Low | CH4 | C | 0.022728 | kg CH4/m3 wastewater | 23.5525 | ton C | 0.8197% | % of incoming C lost as CH4
| Base | Base-Base | CH4 | C | 0.010823 | kg CH4/m3 wastewater | 11.2156 | ton C | 0.8196% | % of incoming C lost as CH4
| Base | Medium-Base | CH4 | C | 0.014998 | kg CH4/m3 wastewater | 15.5417 | ton C | 0.8197% | % of incoming C lost as CH4
| Base | High-Base | CH4 | C | 0.020809 | kg CH4/m3 wastewater | 21.5631 | ton C | 0.8197% | % of incoming C lost as CH4
| Base | Base-High | CH4 | C | 0.010078 | kg CH4/m3 wastewater | 10.4431 | ton C | 0.8196% | % of incoming C lost as CH4
| Base | Medium-High | CH4 | C | 0.014264 | kg CH4/m3 wastewater | 14.7809 | ton C | 0.8192% | % of incoming C lost as CH4
| Base | High-High | CH4 | C | 0.019165 | kg CH4/m3 wastewater | 19.8601 | ton C | 0.8195% | % of incoming C lost as CH4
| Base | Base-Low | N2O | N | 0.0016838 | kg N2O/m3 wastewater | 1.4805 | ton N | 2.676% | % of incoming N lost as N2O
| Base | Medium-Low | N2O | N | 0.0023446 | kg N2O/m3 wastewater | 2.0615 | ton N | 2.674% | % of incoming N lost as N2O
| Base | High-Low | N2O | N | 0.0032757 | kg N2O/m3 wastewater | 2.8801 | ton N | 2.673% | % of incoming N lost as N2O
| Base | Base-Base | N2O | N | 0.0015539 | kg N2O/m3 wastewater | 1.3663 | ton N | 2.674% | % of incoming N lost as N2O
| Base | Medium-Base | N2O | N | 0.0021603 | kg N2O/m3 wastewater | 1.8994 | ton N | 2.674% | % of incoming N lost as N2O
| Base | High-Base | N2O | N | 0.0029976 | kg N2O/m3 wastewater | 2.6356 | ton N | 2.674% | % of incoming N lost as N2O
| Base | Base-High | N2O | N | 0.0014482 | kg N2O/m3 wastewater | 1.2733 | ton N | 2.673% | % of incoming N lost as N2O
| Base | Medium-High | N2O | N | 0.0020248 | kg N2O/m3 wastewater | 1.7803 | ton N | 2.676% | % of incoming N lost as N2O
| Base | High-High | N2O | N | 0.002743 | kg N2O/m3 wastewater | 2.4118 | ton N | 2.674% | % of incoming N lost as N2O
| Base | Base-Low | NH3 | N | 0.0032561 | kg NH3/m3 wastewater | 3.705 | ton N | 6.697% | % of incoming N lost as NH3
| Base | Medium-Low | NH3 | N | 0.0045365 | kg NH3/m3 wastewater | 5.1618 | ton N | 6.696% | % of incoming N lost as NH3
| Base | High-Low | NH3 | N | 0.0063399 | kg NH3/m3 wastewater | 7.2139 | ton N | 6.696% | % of incoming N lost as NH3
| Base | Base-Base | NH3 | N | 0.003007 | kg NH3/m3 wastewater | 3.4216 | ton N | 6.696% | % of incoming N lost as NH3
| Base | Medium-Base | NH3 | N | 0.0041809 | kg NH3/m3 wastewater | 4.7572 | ton N | 6.696% | % of incoming N lost as NH3
| Base | High-Base | NH3 | N | 0.0058013 | kg NH3/m3 wastewater | 6.601 | ton N | 6.696% | % of incoming N lost as NH3
| Base | Base-High | NH3 | N | 0.0028028 | kg NH3/m3 wastewater | 3.1892 | ton N | 6.696% | % of incoming N lost as NH3
| Base | Medium-High | NH3 | N | 0.0039154 | kg NH3/m3 wastewater | 4.4552 | ton N | 6.697% | % of incoming N lost as NH3
| Base | High-High | NH3 | N | 0.0053071 | kg NH3/m3 wastewater | 6.0387 | ton N | 6.696% | % of incoming N lost as NH3
| High | Base-Low | CH4 | C | 0.036216 | kg CH4/m3 wastewater | 37.5291 | ton C | 2.5% | % of incoming C lost as CH4
| High | Medium-Low | CH4 | C | 0.049882 | kg CH4/m3 wastewater | 51.6907 | ton C | 2.5% | % of incoming C lost as CH4
| High | High-Low | CH4 | C | 0.069321 | kg CH4/m3 wastewater | 71.834 | ton C | 2.5% | % of incoming C lost as CH4
| High | Base-Base | CH4 | C | 0.033015 | kg CH4/m3 wastewater | 34.2118 | ton C | 2.5% | % of incoming C lost as CH4
| High | Medium-Base | CH4 | C | 0.045745 | kg CH4/m3 wastewater | 47.4031 | ton C | 2.5% | % of incoming C lost as CH4
| High | High-Base | CH4 | C | 0.063467 | kg CH4/m3 wastewater | 65.7683 | ton C | 2.5% | % of incoming C lost as CH4
| High | Base-High | CH4 | C | 0.030739 | kg CH4/m3 wastewater | 31.8533 | ton C | 2.5% | % of incoming C lost as CH4
| High | Medium-High | CH4 | C | 0.043529 | kg CH4/m3 wastewater | 45.1073 | ton C | 2.5% | % of incoming C lost as CH4
| High | High-High | CH4 | C | 0.058468 | kg CH4/m3 wastewater | 60.5876 | ton C | 2.5% | % of incoming C lost as CH4
| High | Base-Low | N2O | N | 0.0029259 | kg N2O/m3 wastewater | 2.5726 | ton N | 4.65% | % of incoming N lost as N2O
| High | Medium-Low | N2O | N | 0.0040766 | kg N2O/m3 wastewater | 3.5843 | ton N | 4.65% | % of incoming N lost as N2O
| High | High-Low | N2O | N | 0.0056974 | kg N2O/m3 wastewater | 5.0094 | ton N | 4.65% | % of incoming N lost as N2O
| High | Base-Base | N2O | N | 0.0027023 | kg N2O/m3 wastewater | 2.376 | ton N | 4.65% | % of incoming N lost as N2O
| High | Medium-Base | N2O | N | 0.0037571 | kg N2O/m3 wastewater | 3.3034 | ton N | 4.65% | % of incoming N lost as N2O
| High | High-Base | N2O | N | 0.0052133 | kg N2O/m3 wastewater | 4.5838 | ton N | 4.65% | % of incoming N lost as N2O
| High | Base-High | N2O | N | 0.0025188 | kg N2O/m3 wastewater | 2.2147 | ton N | 4.65% | % of incoming N lost as N2O
| High | Medium-High | N2O | N | 0.0035183 | kg N2O/m3 wastewater | 3.0935 | ton N | 4.65% | % of incoming N lost as N2O
| High | High-High | N2O | N | 0.0047692 | kg N2O/m3 wastewater | 4.1933 | ton N | 4.65% | % of incoming N lost as N2O
| High | Base-Low | NH3 | N | 0.0061945 | kg NH3/m3 wastewater | 7.0484 | ton N | 12.74% | % of incoming N lost as NH3
| High | Medium-Low | NH3 | N | 0.0086306 | kg NH3/m3 wastewater | 9.8203 | ton N | 12.74% | % of incoming N lost as NH3
| High | High-Low | NH3 | N | 0.012062 | kg NH3/m3 wastewater | 13.7248 | ton N | 12.74% | % of incoming N lost as NH3
| High | Base-Base | NH3 | N | 0.005721 | kg NH3/m3 wastewater | 6.5096 | ton N | 12.74% | % of incoming N lost as NH3
| High | Medium-Base | NH3 | N | 0.0079542 | kg NH3/m3 wastewater | 9.0507 | ton N | 12.74% | % of incoming N lost as NH3
| High | High-Base | NH3 | N | 0.011037 | kg NH3/m3 wastewater | 12.5586 | ton N | 12.74% | % of incoming N lost as NH3
| High | Base-High | NH3 | N | 0.0053326 | kg NH3/m3 wastewater | 6.0677 | ton N | 12.74% | % of incoming N lost as NH3
| High | Medium-High | NH3 | N | 0.0074486 | kg NH3/m3 wastewater | 8.4754 | ton N | 12.74% | % of incoming N lost as NH3
| High | High-High | NH3 | N | 0.010097 | kg NH3/m3 wastewater | 11.4887 | ton N | 12.74% | % of incoming N lost as NH3
| All | Base-Low | CO | C | 0.0010141 | kg CO/m3 wastewater | 0.60047 | ton C | 0.04% | % of incoming C lost as CO
| All | Medium-Low | CO | C | 0.0013967 | kg CO/m3 wastewater | 0.82705 | ton C | 0.04% | % of incoming C lost as CO
| All | High-Low | CO | C | 0.001941 | kg CO/m3 wastewater | 1.1493 | ton C | 0.04% | % of incoming C lost as CO
| All | Base-Base | CO | C | 0.00092441 | kg CO/m3 wastewater | 0.54739 | ton C | 0.04% | % of incoming C lost as CO
| All | Medium-Base | CO | C | 0.0012808 | kg CO/m3 wastewater | 0.75845 | ton C | 0.04% | % of incoming C lost as CO
| All | High-Base | CO | C | 0.0017771 | kg CO/m3 wastewater | 1.0523 | ton C | 0.04% | % of incoming C lost as CO
| All | Base-High | CO | C | 0.00086069 | kg CO/m3 wastewater | 0.50965 | ton C | 0.04% | % of incoming C lost as CO
| All | Medium-High | CO | C | 0.0012188 | kg CO/m3 wastewater | 0.72172 | ton C | 0.04% | % of incoming C lost as CO
| All | High-High | CO | C | 0.0016371 | kg CO/m3 wastewater | 0.9694 | ton C | 0.04% | % of incoming C lost as CO
| All | Base-Low | NMVOCs | n.a. | 0.00019052 | kg NMVOCs/m3 wastewater | n.a. | n.a. | n.a. | n.a.
| All | Medium-Low | NMVOCs | n.a. | 0.00026521 | kg NMVOCs/m3 wastewater | n.a. | n.a. | n.a. | n.a.
| All | High-Low | NMVOCs | n.a. | 0.00037044 | kg NMVOCs/m3 wastewater | n.a. | n.a. | n.a. | n.a.
| All | Base-Base | NMVOCs | n.a. | 0.00017574 | kg NMVOCs/m3 wastewater | n.a. | n.a. | n.a. | n.a.
| All | Medium-Base | NMVOCs | n.a. | 0.00024434 | kg NMVOCs/m3 wastewater | n.a. | n.a. | n.a. | n.a.
| All | High-Base | NMVOCs | n.a. | 0.00033904 | kg NMVOCs/m3 wastewater | n.a. | n.a. | n.a. | n.a.
| All | Base-High | NMVOCs | n.a. | 0.00016372 | kg NMVOCs/m3 wastewater | n.a. | n.a. | n.a. | n.a.
| All | Medium-High | NMVOCs | n.a. | 0.00022912 | kg NMVOCs/m3 wastewater | n.a. | n.a. | n.a. | n.a.
| All | High-High | NMVOCs | n.a. | 0.00031025 | kg NMVOCs/m3 wastewater | n.a. | n.a. | n.a. | n.a.

## AD Return Flow
Impact of AD and Belt Filter Press Supernatant on BOD and N Loading to Secondary Treatment
Calculates the quantity of N and BOD returning to headworks and the increased oxygen demand, aeration requirement, of treating additional loading.
| Feedstock Scenarios - gallons prior to dewatering (if applicable) |  |  |  |  | Influent Wastewater Nitrogen Concentrations
| Waste Type | Base | Medium | High |  | Biological Oxygen Demand | 323 | mg/L | calculated, Brake 2007
| Primary Sludge | 17654 | 17654.2014 | 17654.2014 |  | Total Kjeldahl Nitrogen (TKN) | 56 | mg/L N | Bath Influent Sampling Oct 2011-Oct 2015
| Waste Activated Sludge | 75556.9523 | 75556.9523 | 75556.9523 |  | Ammonia | 32 | mg/L N | Bath Influent Sampling Oct 2011-Oct 2015
| Septic Waste | 14000 | 14000 | 14000 |  | Total Phosphorus (TP) | 8 | mg/L P | DC WWTP Basics R63
| Slaughterhouse Waste | 0 | 1000 | 4000 |  | Nitrite | 0.5 | mg/L N | Cunningham 2016
| Cheese Waste | 0 | 2000 | 3000 |  | Nitrate | 0.5 | mg/L N | Cunningham 2016
| Winery Waste, Vinasse | 0 | 1000 | 1000
| Portable Toilet Waste | 2000 | 2000 | 2000 |  | Flowrate | 1 | MGD
| Nitrogen to AD |  |  |  |  | Total N loading (as N) | 474.012 | lb/day
| Waste Type | Base | Medium | High |  | Total N O2 demand | 2014.551 | lb/day
| Primary Sludge | 70.7328 | 70.7328 | 70.7328
| Waste Activated Sludge | 127.0618 | 127.0618 | 127.0618 |  | HSOW Waste Characteristics
| Septic Waste | 12.034 | 12.034 | 12.034 |  | HSOW Constituent | Slaughterhouse Waste | Cheese Waste | Winery Waste, Vinasse
| Slaughterhouse Waste | 0 | 12.5002 | 50.0008 |  | BOD | 40000 | 44940 | 14542
| Cheese Waste | 0 | 17.0003 | 25.5004 |  | Soluble BOD | 106.6667 | 119.84 | 38.7787
| Winery Waste, Vinasse | 0 | 0.87501 | 0.87501 |  | COD | 80000 | 74900 | 50207
| Portable Toilet Waste | 15.6392 | 15.6392 | 15.6392 |  | Soluble COD | 4000 | 449.4 | 301.242
| *Assume minimal NO3/NO2, therefore TKN = TN |  |  |  |  | TKN | 1500 | 1020 | 105
[6 empty] | Soluble TKN | 804.1237 | 546.8041 | 56.2887
| *N is conserved in the Anaerobic Digester |  |  |  |  | Ammonia | 773.1959 | 60 | 54.1237
[6 empty] | Nitrite | 0 | 0 | 0
| Fraction of N in liquid | 0.5 | 0.5 | 0.5 |  | Nitrate | 0 | 0 | 0
| N moving on to composting (lb/day) | 112.7339 | 127.9216 | 150.922 |  | Total phosphorus | 800 | 300 | 800
| Increase in N to Secondary (lb/day) | 0 | 15.1877 | 38.1881
| Percent Increase in N loading (@ headworks) | 0 | 3.204% | 8.056%
| Added NH3 removal (lb/day) | 0 | 18.4423 | 46.3713
| Added Oxygen Demand (lb/day) | 0 | 78.3796 | 197.0779
BOD to AD
| Waste Type | Base | Medium | High |  | Oxygen Demand | 4.25 | lb O2/lb NH3 Nitrified
| Primary Sludge | 1745.9442 | 1745.9442 | 1745.9442
| Waste Activated Sludge | 1003.1193 | 1003.1193 | 1003.1193
| Septic Waste | 62.1563 | 62.1563 | 62.1563 |  | Influent BOD Loading | 2686.068 | lb/day
| Slaughterhouse Waste | 0 | 333.3385 | 1333.3542
| Cheese Waste | 0 | 749.0117 | 1123.5176
| Winery Waste, Vinasse | 0 | 121.1852 | 121.1852
| Portable Toilet Waste | 53.5773 | 53.5773 | 53.5773
| BOD removal in AD1 | 88.7% | 88.7% | 88.7%
| Fraction of BOD in Liquid2 | 10% | 10% | 10% | returns to headworks
| Return of BOD to Secondary (lb/day) | 32.3722 | 45.9722 | 61.5043
| Increased BOD to Secondary (lb/day) | 0 | 13.6 | 29.132
| Percent Increase in BOD loading @ headworks | 0% | 0.5063% | 1.085%
1-CAPDETWorks, Harris et al. 1982
2-Appleton and Rauch Williams 2017, assumed to partition equivalent to COD
| Total Added O2 demand per scenario (lb/day) | 0 | 91.9795 | 226.2099
| Percent increase in O2 demand as compared to baseline | 0% | 1.957% | 4.812% | >>used to scale blower electricity demand in LCI model.

## PortableT Septage
Portable Toilet Septage
Assumed Values
| Characteristic | Value | Unit | Source
| Biogas Applied Yield | 3.9 | scf CH4/lb VS applied | Clearcove BMP Testing
| Biogas Destructive Yield | 4.6 | scf CH4/lb VS destroyed | Clearcove BMP Testing
| Solids Content in Raw Sludge | 3310 | mg/L | ALS 2015, Affordable Portable
| Volatile Solids Content in Raw Sludge | 1420 | mg/L | ALS 2015, Affordable Portable
| VS | 0.429 | (%) | ALS 2015, Affordable Portable
| Total Solids | 0.33066 | % by mass | calculated
| BOD | 3210 | mg/L | ALS 2015, Affordable Portable
| Ammonia | 814 | mg/L | ALS 2015, Affordable Portable
| COD | 5180 | mg/L | ALS 2015, Affordable Portable
| TKN | 937 | mg/L | ALS 2015, Affordable Portable
| Phosphorus, Total | 67.7 | mg/L | ALS 2015, Affordable Portable
| Copper | 0.317 | mg/L | ALS 2015, Affordable Portable
| Specific Gravity | 1.001 |  | based on calculated value for WAS
| Specific Gravity of Solids | 1.4518 |  | calculated
** ALS 2015 also contains metals content data. None of the values approached inhibition limits.

## Bath WAS
Waste Activated Sludge
| Assumed Values |  |  |  | Alternative Values
| Characteristic | Value | Unit | Source | Value | Unit | Source
| Biogas Applied Yield | 1.4 | scf CH4/lb VS applied | Clearcove BMP Testing
| Biogas Destructive Yield | 1.6 | scf CH4/lb VS destroyed | Clearcove BMP Testing
| Solids Content in Raw Sludge | 0.5 | % | GHD 2015 | 0.8 (0.4-1.2) | % of TS | Tchobanoglous et al. 2014, pg. 1455
| Volatile Solids | 30.7692 | % | CRA 2015 | 70 | % of TS | Tchobanoglous et al. 2014, pg. 1455
| Specific Gravity of Solids | 1.25 |  | Tchobanoglous et al. 2014, pg. 1457
| Specific Gravity of Sludge | 1.0012 |  | calculated | 1.05 |  | Tchobanoglous et al. 2014, pg. 1457
| Total Nitrogen, as N | 3.8 | % of TS | Tchobanoglous et al. 2014, pg. 1455
| BOD | 30 | % of TS
| Total P, as P | 2.4002 | % of TS | Tchobanoglous et al. 2014, pg. 1455
| Total Nitrogen | 190.2375 | mg/L | calculated
| Total P | 120.1592 | mg/L | calculated

## Bath Primary Sludge
Primary Sludge
| Assumed Values |  |  |  | Alternative Values
| Characteristic | Value | Unit | Source | Value | Unit | Source
| Biogas Applied Yield | 2.8 | scf CH4/lb VS applied | Clearcove BMP Testing
| Biogas Destructive Yield | 10.8 | scf CH4/lb VS destroyed | Clearcove BMP Testing
| Solids Content in Raw Sludge | 1.8 | % by mass | GHD 2015 | 3 | % | Tchobanoglous et al. 2014, pg. 1455
| Volatile Solids | 68.1818 | % | CRA 2015 | 75 | % | Tchobanoglous et al. 2014, pg. 1455
| Specific Gravity of Solids | 1.4 |  | Tchobanoglous et al. 2014, pg. 1457
| Specific Gravity of Sludge | 1.0072 |  | calculated | 1.02 |  | Tchobanoglous et al. 2014, pg. 1457
| Nitrogen, as N | 2.5 | % of TS | Tchobanoglous et al. 2014, pg. 1455
| Cellulose | 10 | % of TS | Tchobanoglous et al. 2014, pg. 1455 | 8 to 15 | % of TS | Tchobanoglous et al. 2014, pg. 1455
| Protein | 25 | % of TS | Tchobanoglous et al. 2014, pg. 1456 | 20-30 | % of TS | Tchobanoglous et al. 2014, pg. 1455
| Total P, as P | 0.69824 | % of TS | Tchobanoglous et al. 2014, pg. 1455
| Total Nitrogen | 453.24 | mg/L | calculated
| Total P | 126.5872 | mg/L | calculated

## Slaughterhouse Waste
Slaughterhouse Waste - Animal Rendings
| Assumed Values |  |  |  | Alternative Reference Values
| Characteristic | Value | Unit | Source | Value | Unit | Source
| Biogas Applied Yield | 400 | m3 CH4/ton VS | Luste and Luostarinen 2010 | 2.8 | scf CH4/lb VS applied | CCS BMP Testing, BMP results not meant to be used in biogas generation calculations, animal rendings
| Average VS Destruction | 38% |  | Luste and Luostarinen 2010 | 3.5 | scf CH4/lb VS destroyed | CCS BMP Testing, BMP results not meant to be used in biogas generation calculations, animal rendings
| Biogas Destructive Yield | 1052.6316 | m3 CH4/ton VS | calculated
| Total Solids | 13 | % by mass | Luste and Luostarinen 2010
| Volatile Solids | 12 | % by mass | Luste and Luostarinen 2010
| VS | 92.31% | % of TS | Luste and Luostarinen 2010
| COD, soluble | 4000 | mg/L | Luste and Luostarinen 2010
| Specific Gravity of DTC | 1.05
| pH | - |  |  | 6.5-8
| Total Solids | 136500 | mg/L | calculated
| BOD | 30000-50000 | mg/L | https://books.google.com/books?id=W0EqBgAAQBAJ&pg=PA93&lpg=PA93&dq=COD+of+digestive+tract+waste&source=bl&ots=JZHDdtOEJc&sig=ZqCo0oqbo50WHq9uQWUyHn-FIj8&hl=en&sa=X&ved=0ahUKEwj7x9fE9qHTAhXGRY8KHdzYAHgQ6AEIQTAH#v=onepage&q=COD%20of%20digestive%20tract%20waste&f=false
| Global Slaughterhouse Mixture | 1868.9439 | mg/L TKN | Palatsi et al. 2011, originally reported in g/kg
| Animal Rending Wastewater | 500-1000 | mg/L TKN | Sindt 2006
| Total Nitrogen1 | 1500 | mg/L | between Palatsi et al. 2011 and Sindt 2006
1 Nitrate/nitrate is assumed negligible (De Guardia et al. 2009)

## Winery Waste
Winery Waste - Vinasse
Assumed Values
| Characteristic | Value | Unit | Source
| Total Solids | 38485 | mg/L | Bustamante et al. 2005
| Total Solids | 0.037473 | % total mass | calculated
| Volatile Solids | 23197 | mg/L | Bustamante et al. 2005
| VS | 0.60275 | % of TS | calculated
| COD, soluble | 50207 | mg O2/L | Bustamante et al. 2005
| Density, Vinasse | 1.027 | g/cm3 | Bustamante et al. 2005
| BOD5 | 14542 | mg O2/L | Bustamante et al. 2005
| COD/BOD5 Ratio | 3.4526 |  | calculated
| Density of Vinasse Solids | 1.7205 | g/cm3 (also s.g.) | calculated
| Nitrogen, Total | 105 | mg/L | Bustamante et al. 2005

## Cheese Waste
Cheese Waste - Whey
| Assumed Values |  |  |  | Alternative Reference Values
| Characteristic | Value | Unit | Source | Value | Unit | Source
| Biogas Applied Yield | 0.83 | m3 biogas/kg volatile dry solids | Gelegenis et al. 2007 | 2.4 | scf CH4/lb VS applied | Kraft Innoculum', CCS BMP Testing, BMP results not meant to be used in biogas generation calculations
| Average VS Destruction |  |  |  | 5 | scf CH4/lb VS destroyed | Kraft Innoculum', CCS BMP Testing, BMP results not meant to be used in biogas generation calculations
| Total Solids | 7.8 | % total mass | Gelegenis et al. 2007
| Volatile Solids | 4.8 | % total mass | Gelegenis et al. 2007
| VS | 0.61538 | % of TS | calculated
| COD | 74900 | mg O2/L | Gelegenis et al. 2007
| Density of Whey Solids | not in feedstock mix | g/cm3 (also s.g.) | calculated
| specific gravity - sweet whey | 1.025 | % of TS
| Nitrogen, Total | 1020 | mg/L | Gelegenis et al. 2007
| Nitrogen, Total | 0.00013077
| Ammonia (as N) | 60 | mg/L | Gelegenis et al. 2007
| Phosphorus | 300 | mg/L | Gelegenis et al. 2007
| Phosphorus | 3.8462e-05 | % of TS
| C:N | 24.1 |  | Gelegenis et al. 2007

## HSOW Biogas
Waste Type | Low Yield | High Yield | Low/High Yield Units | Biogas Yield (m3/kg VS destroyed) | Source
Harvest Residues | 375 |  | m3/ton organic waste solids |  | Braun and Wellinger 2003
Animal Manures | 200 | 500 | m3/ton organic waste solids |  | Braun and Wellinger 2003
Yeast products (Winery/Brewery) | 400 | 800 | m3/ton organic waste solids |  | Braun and Wellinger 2003
Old animal feed | 500 | 650 | m3/ton organic waste solids |  | Braun and Wellinger 2003
Slaughterhouse waste | 550 | 1100 | m3/ton organic waste solids | 1.4896 | Braun and Wellinger 2003
Plant Oil | 1000 |  | m3/ton organic waste solids |  | Braun and Wellinger 2003
Paper Industry Waste | 400 | 800 | m3/ton organic waste solids |  | Braun and Wellinger 2003
Sewage Sludge | 250 | 350 | m3/ton organic waste solids | 1 | Braun and Wellinger 2003
Winery Vinasse | 0.35 | 0.7 | m3/kg VS |  | Belhadj et al. 2013
Cheese Whey | 0.1366 | 0.2163 | m3/kg VS |  | Jasko et al. 2011
Cheese Whey | 337 | 388 | L CH4/kg VS |  | Jasko et al. 2011

## References
Number | Citation | Reference
1 | ALS 2015 | ALS Group USA. 2015. Analytical Report on incoming septage waste. Performed for Bath Wastewater Treatment Facility.
2 | Appleton and Rauch-Williams 2017 | Appleton, A.R., and T. Rauch-Williams. 2017. Co-Digestion of Organic Waste Addressing Operational Side-Effects. Prepared for Water Environment Research Foundation (WERF).
3 | Belhadj et al. 2013 | Belhadj, S., F. Karouach, H. El Bari, Y. Joute. 2013. The biogas production from mesophilic anaerobic digestion of vinasse. Journal Of Environmental Science, Toxicology And Food Technology. 5(6): 72-77.
4 | Bond 2011 | Bond, T., and Templeton, M.R. 2011. History and future of domestic biogas plants in the developing world. Energy for Sustainable Development. 15. 347-354.
5 | Bothi 2007 | Bothi, K.L. 2007. Characterization of Biogas from Anaerobically Digested Dairy Waste for Energy Use. Master's Thesis, Cornell University, Ithaca, New York.
6 | Brake 2007 | Brake, P. 2007. A Bug’s-Eye-View of the BOD Test. http://www.perrybrake.com/BODBook.‌html Accessed 30 August, 2016.
7 | Braun and Wellinger 2003 | Braun, R., and A. Wellinger. 2003. Potential of Co-Digestion. International Energy Agency. http://www.iea-biogas.net/files/daten-redaktion/download/publi-task37/Potential%20of%20Codigestion%20short%20Brosch221203.pdf. Accessed 30 June, 2016.
8 | Brown et al. 2009 | Brown, S., M. Cotton, S. Messner, F. Berry, and D. Norem. 2009. Issue Paper: Methane avoidance from composting. http://faculty.washington.edu/slb/docs/CCAR_‌Composting_issue_paper.pdf Accessed 9 September 2016.
9 | Bustamante et al. 2005 | Bustamente, M.A., Paredes, C., Moral, R., Moreno-Caselles, J., Perez-Espinosa, A., and Perez-Murcia, M.D. 2005. Uses of winery and distillery effluents in agriculture: characterization of nutrient and hazardous components. Water Science and Technology. 51(1):145-151.
10 | CCME 2009 | CCME (Canadian Council of Ministers of the Environment). 2009. Biosolids Emissions Assessment Model (BEAM): User Guide. http://www.ccme.ca/files/Resources‌/waste/biosolids/‌beam_user_guide_1430.pdf Accessed 10 April, 2017.
11 | CRA 2015 | CRA (Conestoga-Rovers & Associates). 2015. Village of Bath WWTP Upgrades Final Engineering Report. Prepared for: Bath Electric Gas & Water Systems. Bath, New York.
12 | Cunningham 2016 | Cunningham, E. 2016. Personal communication with Erin Cunningham. GHD Engineering. 14 June, 2016.
13 | CWMI 1990 | CWMI (Cornell Waste Management Institute). 1990. Yard Waste Composting. http://compost.css.cornell.edu/yardwastecomposting2.pdf Accessed 9 September, 2016.
14 | De Guardia et al. 2009 | De Guardia, A., P. Mallard, C. Teglia, A. Marin, C. Le Pape, et al. 2009. Comparison of Five Organic Wastes Regarding their Behaviour During Composting: Part 1, Biodegradability, Stabilization Kinetics and Temperature Rise. Waste Management. https://hal.archives-ouvertes.fr/hal-00455647/document Accessed 9 May, 2017.
15 | Fukumoto et al. 2003 | Fukumoto, Y., T. Osada, D. Hanajima, and K. Haga. 2003. Patterns and qantities of NH3, N2O, and CH4 emissions during swine manure compositing without forced aeroation - effect of composti pile scale.
16 | Gelegenis et al. 2007 | Gelegenis, J., Georgakakis, D., Angelidaki, I., and Mavris, V. 2007. Optimization of biogas production by co-digesting whey with diluted poultry manure. Renewable Energy. 32: 2147-2160.
17 | GHD 2015 | GHD. 2015b. Preliminary Solids Handling Basis of Design at Maximum Month Conditions.
18 | GHD 2016 | GHD Consulting. 2016. Life Cycle Cost Analysis Evaluation: Preliminary and Primary Treatment Processes Village of Bath WWTP. Prepared for Gath Electric Gas & Water Systems.
19 | Hansen et al. 1998 | Hansen, K., Angelidaki, Ahring B., 1998. Anaerobic digestion of swine manure: Inhibition by ammonia. Water Resources. 32(1): 5-12.
20 | Harris and Phillips 1986 | Harris, R.A., and D.R. Phillips. 1986. Density of Selected Wood Fuels. http://www.gfc.state.ga.us/resources/publications/research-papers/GFRP61.pdf Accessed 18 August 2016.
21 | Harris et al. 1982 | Harris, R.W., M.J. Cullinane, P.T. Sun. 1982. Proces Design and Cost Estimating Algorithms for the Computer Assisted Procedure for Design and Evaluation of Wastewater Treatment Systems: Technical Reference. Prepared for U.S. EPA. PB82-190455
22 | Hellebrand 1998 | Hellebrand, H.J. 1998. Emission of N2O and other Trace Gases during Composting of Grass and Green Waste. Journal of Agricultural Engineering Research. 96: 365-375
23 | Hellmann et al. 1997 | Hellmann, L. Zelles, A. Palojarvi, and Q. Bai. 1997. Emission of Climate-Relevant Trace Gases and Succession of Microbial Communities during Open-Windrow Composting
24 | IEA 2009 | IEA (International Energy Agency). 2009. Biogas from slaughterhouse waste: towards an energy self-sufficient industry. http://www.iea-biogas.net/success-stories.html?file=files/daten-redaktion/download/Success%20Stories/st_martin.pdf. Accessed 30 June, 2016.
25 | Jasko et al. 2011 | Jasko, J., E. Skripsts, V. Dubrovskis, E. Zabarovskis, and V. Kotelenecs. 2011. Biogas production from Cheese Whey in Two Phase Anaerobic Digestion. Presented at Engineering for Rural Development Conference, Jelgava, Latvia.
26 | Luste and Luostarinen 2010 | Luste, S., and Luostarinen, S. 2010. Anaerobic co-digestion of meat-processing by-products and sewage sludge - Effect of hygienization and OLR. Bioresource Technology. 101: 2657-2664.
27 | Maulini-Duran et al. 2013 | Maulini-Duran, C. A. Artola, X. Font, and A. Sanchez. 2013. A systematic study of the gaseous emissions from biosolids composting: Raw sludge versus anaerobically digested sludge. Bioresource Technology. 147: 43-51.
28 | Milczarek et al. 2013 | Milczarek, M., Neczaj, E., Parkitna, K., and Worwag, M. 2013. Indicators influencing the course of the thermophilic phase of composting process. In Ecological Engineering IV, edited by Pawlowski et al. Taylor & Francis Group: London. https://books.google.com/books?id=ZOrZg_ROH2oC&pg=PA244&lpg=PA244&dq=moisture+content+requirement+biosolids+composting&source=bl&ots=bF36obDeLH&sig=Ro_Dq768owJaUOuk3o6nZWGtldA&hl=en&sa=X&ved=0ahUKEwid36vq_5PNAhUFGD4KHUfqBE8Q6AEIPjAE#v=onepage&q=moisture%20content%20requirement%20biosolids%20composting&f=false
29 | Palatsi et al. 2011 | Palatsi, J., M. Vinas, B. Fernandez, and X. Flotats. 2011. Anaerobic Digestion of Slaughterhouse Waste: Main Process Limitations and Microbial Community Interactions. Bioresource Technology. 102(3). 2219-2227.
30 | Potter et al. 2006 | Potter, S. R., S. Andrews, J.D. Atwood, R.L. Kellogg, J. Lemunyon, L. Norfleet, D. Oman. 2006. Model Simulation of Soil Loss, Nutrient Loss, and Change in Soil Orgnaic Carbon Associated with Crop Production. United States Department of Agriculture, Natural Resources Conservation Service. https://www.nrcs.usda.gov/Internet/FSE_DOCUMENTS/nrcs143_013138.pdf Accessed 14 April. 2017.
31 | Richard 2014 | Richard, T. 2014. Moisture and Carboon/Nitrogen Ratio Calculations Spreadsheet. http://compost.css.cornell.edu/download.html Accessed 9 September 2016.
32 | Rico et al. 2014 | Rico, C., R. Diego, A. Valcarce, and J.L. Rico. 2014. Biogas Production from Various Typical Organic Wastes Generated in the Region of Cantabria (Spain): Methane Yields and Co-Digestion Tests. Smart Grid and Renewable Energy. 5: 128-136.
33 | ROU 2006 | ROU (Recycled Organics Unit). 2006. Life Cycle Inventory and Life Cycle Assessment for Windrow Composting Systems. Prepared for Department of Environment and Conservation, Sydney, Australia.
34 | Sindt 2006 | Sindt, L.G. 2006. Environmental issues in the rendering industry, in: D. Meeker (Ed.), Essential Rendering, National Renderers Association, Washington DC. pp. 245–258.
35 | Stamatelatou et al. 2012 | Stamatelatou, K., N. Giantsiou, V. Diamantis, C. Alexandridis, A. Alexandridis, and A. Aivasidis. 2012. Anaerobic Digestion of Cheese Whey Wastewater through a Two Stage System. Presented at the 3rd International Conference of Industrial and Hazardous Waste Management, Crete, Greece
36 | SYLVIS 2011 (BEAM Model) | SYLVIS Environmental. 2011. The Bioslids Emissions Assessment Model (BEAM). Version 1.1. Prepared for the Canadian Council of Ministers of the Environment.
37 | Takacs and Vanrolleghem 2006 | Takacs, I., and Vanrolleghem, P.A. 2006. Elemental Balances in Activated Sludge Modelling. IWA Publishing, London, UK.
38 | Tchobanoglous et al. 2014 | Tchobanoglous, G., Stensel, H.D., Tschihashi, R., and Burton, F. Wastewater Engineering Treatment and Resource Recovery. McGraw Hill. New York.
39 | Williams 2009 | Williams, T.O. 2009. The Next Generation of Aerated Static Pile Biosolids Composting Facilities. US Composting Council 17th Annual Conference and Tradeshow, Houston, TX. http://compostingcouncil.org/wp/wp-content/uploads/2013/02/Williams1.pdf Accessed 14 April, 2017.
40 | Wiser et al. 2010 | Wiser, J.R., J.W. Schettler, and J.L. Willis. 2010. Evaluation of Combined Heat and Power Technologies for Wastewater Treatment Facilities. Prepared for Columbus Water Works, Columbus, GA. EPA 832-R-10-006.

## Conversion Factors
Conversion Factors Used within this workbook
Conversion Factors
| Conversion Description | Value | Units | Equivalent Value | Equivalent Value Units | Source/Note
| gal/m3 | 264.172
| lb/kg | 2.2046
| m/mile | 1609.34
| ft3/m3 | 35.3147
| Water Density | 999.97 | kg/m³ |  |  | 40-50ºF
| sqft/m2 | 10.7639
| MJ/kWh | 3.6
| BTU/MJ | 947.7778
| Natural Gas | 38.2 | MJ/m3
| BOD/cBOD ratio | 1.16 |  |  |  | Brake 2007
| bCOD/BOD ratio | 1.6
| L/gal | 3.7854
| lb/gal water | 8.34
| 1 cubic meter = | 1000 | cubic decimeters
| 1 L = | 1000 | cubic centimeter
| 1 g = | 1000 | mg
| MJ/cubic foot CH4 | 1.0657 | MJ/ft3
| 1 metric ton = | 1000 | kg
| m3/yd3 | 0.76455
| Methane Heat Content | 0.94537 | MJ/ft3 (LHV at ambient (68*F 1 atm)) | 896 | BTU/ft3 | Marks’ Standard Handbook for Mechanical Engineers, eighth edition
| COD/VSS ratio | 1.42 | COD/VSS |  |  | Takacs and Vanrolleghem 2006
| Natural Gas Heat Content | 1027 | BTU/ft3 |  |  | MIT Energy Conversion Sheet
| 1 cubic meter = | 1000 | Liters
| Feedstock Scenario Drop Down | Base | Medium | High | Custom
| AD Operation Scenario Drop Down | Low | Base | High
| Compost Emission Scenarios | Low | Base | High
| Amendment Scenarios | Yes | No