## TOC
Drinking Water Treatment (DWT) Cost Calculations
Table of Contents
Data Inputs | Serves as the source for all data inputs for these cost calculations. Data inputs include data received from GCWW and FTT and assumptions made.
Unit Process Costs | Calculates the annual and unit costs for each unit operation. Also calculates chemical unit costs using the annual cost and average annual amount used reported by GCWW.
Sludge Calculations | Calculates the sludge produced for both the base case and Ferrate case using data input from GCWW and FTT and a calculation methodology from AWWA (2002).
Chemical Unit Costs | Compiles the unit costs for the chemicals provided by GCWW (calculated in the Unit Process Costs worksheet). Then calculates the unit cost of ferrate solution based on the unit cost of feedstocks.
Cost Calculations | Compiles the revenues and productivity data provided by GCWW and calculates total costs (using costs calculated in Cost Calculations worksheet). Changes in total cost for Ferrate cases are compared to the base case costs.
Sensitivity Analysis | Performs the cost sensitivity analyses. These calculations only focus on costs for the unit operations subject to the sensitivity analysis. Sensitivity analyses performed using Monte Carlo simulations using @Risk. If the user does not have @Risk, then @Risk formulas will appear as the "#NAME?" error in Excel. @Risk results are provided in separate spreadsheets.
Results | Compiles final cost results (total annual costs and normalized costs) for each life cycle stage.
Data Quality Information | Provides documentation of data quality notes for the data quality criteria outlined in the project QAPP.

## Data Inputs
Productivity Data | [6 empty] | Notes
Total Finished Water Produced (gal/yr) | 44396000000 | [5 empty] | Annual volumes of water produced and sold were provided by GCWW.
Surface Water Plant Finished Water Produced (gal/yr) | 38747000000
Direct Residential Sales (both plants) (gal/yr) | 17950000000
Direct Non-residential Sales (both plants) (gal/yr) | 13610000000
Wholesale Sales (both plants) (gal/yr) | 5840000000
Revenues (both plants)
Direct Residential Sales ($/yr) | 66500000 | [5 empty] | All data provided by GCWW.
Direct Non-residential Sales ($/yr) | 31100000
Wholesale Sales ($/yr) | 15750000
Fees/Other Revenues ($/yr) | 5840000 | [5 empty] | Connection/development fees plus other.
Total Revenues ($/yr) | 119190000
| Amount |  |  | Basis of Amount |  | Total Cost ($)
| Average | Min | Max | Description (unit) | Value
Base Case Unit Process Costs | [6 empty] | All data provided by GCWW.
Source Water Acquisition
None | -- | -- | -- | -- | -- | --
Flocculation
Alum (lb) | 0.962 | 0.682 | 1.351 | Unit water produced (ft3) | 1000 | 888675 | Annual cost reported by GCWW.
Polymer (lb) | 0.096 | 0.062 | 0.161 | Unit water produced (ft3) | 1000 | 94000 | Annual cost reported by GCWW.
Sedimentation
Sludge Produced (lb) | 3.5574 | 0.57268 | 15.3822 | Unit water produced (ft3) | 1000 | 15000 | Annual cost reported by GCWW. Amount of sludge calculated on "Sludge Calculations" worksheet.
Lime Addition
Lime (lb) | 0.177 | 0.046 | 0.291 | Unit water produced (ft3) | 1000 | 53985 | Annual cost reported by GCWW.
Sand Filtration
Sand Replacement (lb) | 0.428 | -- | -- | Unit water produced (ft3) | 1000
Waste Sand Disposal | -- | -- | -- |  |  | 30000 | Annual cost reported by GCWW.
GAC Adsorption
GAC Replacement (lb) | 0.156 | -- | -- | Unit water produced (ft3) | 1000 | 1070955 | Annual cost reported by GCWW.
GAC Regeneration
Natural Gas (purchased) (scf) | 75600000 | -- | -- | Surface water plant water produced (gal) | 38747000000 | -- | 42,000 ccf NG/reg; 1ccf = 100 ft3; basis = volume finished water
Number of Regenerations per Year | 18 | -- | -- | Surface water plant water produced (gal) | 38747000000 | --
GAC NSF Cost | -- | -- | -- | -- | -- | 11500 | Annual cost reported by GCWW.
Air Permit for GAC | -- | -- | -- | -- | -- | 4000 | Annual cost reported by GCWW.
Conditioning
Caustic Soda (lb) | 1.073 | 0.617 | 2.163 | Unit water produced (ft3) | 1000 | 639756 | Annual cost reported by GCWW.
Sodium Hexametaphosphate (lb) | 0.121 | 0.082 | 0.173 | Unit water produced (ft3) | 1000 | 258687 | Annual cost reported by GCWW.
Disinfection
Gaseous Chlorine (lb) | 0.11 | 0.08 | 0.161 | Unit water produced (ft3) | 1000 | 117926 | Annual cost reported by GCWW.
Maintenance | -- | -- | -- | -- | -- | 10000 | Annual cost for maintenance of disinfection unit reported by GCWW.
Risk Management Plan Cost | -- | -- | -- | -- | -- | 200 | Annual RMP compliance cost for gaseous chlorine reported by GCWW.
Fluoridation
Hydrofluorosilicic Acid (lb) | 0.237 | 0.19 | 0.341 | Unit water produced (ft3) | 1000 | 364796 | Annual cost reported by GCWW.
Distribution
Electricity (kWh) | 76137689 | -- | -- | Surface water plant water produced (gal) | 38747000000 | --
Sodium Hypochlorite (lb) | 0.023 | 0.01 | 0.042 | Unit water produced (ft3) | 1000 | 10896 | Annual cost reported by GCWW.
Facility-Wide Costs
Labor |  |  |  | Surface water plant water produced (gal) | 38747000000 | 1822389.855 | Annual cost for staff operating treatment facility reported by GCWW.
Maintenance (total) | -- | -- | -- | -- | -- | 400000 | Total annual maintenance cost provided by GCWW.
Electricity (at plant) (purchased) (kWh) | 39125286 | -- | -- | Surface water plant water produced (gal) | 38747000000 | --
Electricity Unit Cost ($/kWh) | -- | -- | -- | -- | -- | 0.0328
Electricity (at plant) (cogen) (kWh) | 2287186 | -- | -- | Surface water plant water produced (gal) | 38747000000 | 0 | Generated by waterwheels. No associated costs.
Natural Gas Unit Cost ($/scf) | -- | -- | -- | -- | -- | 0.005668 | Natural gas unit cost is $0.5668/ccf. 1 ccf = 100 ft3.
Other
Municipal Bond Rate (%) | 6% | 4% | 8% | -- | -- | --
Ferrator Unit Process Costs | [6 empty] | All data provided by FTT except where noted.
Capital Costs
Model Fe300 Ferrators | -- | -- | -- | Unit | 1 | 810000 | Capital cost per unit.
Ferrator Monitors | -- | -- | -- | Unit | 1 | 20000 | Capital cost per unit.
Ferrator Lifetime (yr) | 15 | -- | -- | Unit | 1 | --
Piping | -- | -- | -- | Ferrator unit | 1 | 202500 | Ancillary capital cost estimated as 25% from AWWA (2008). This factor is applied to the Ferrator unit cost.
Pumps | -- | -- | --
Electrical Equipment | -- | -- | --
Building | -- | -- | --
Chemical Feedstock Storage Tanks | -- | -- | --
Utilities and Maintenance
Electricity (kWh) | 91250 | -- | -- | Ferrator unit | 6
Incidental Repairs | -- | -- | -- | Ferrator unit | 6 | 97200 | FTT estimated incidental repairs would cost about 2% of the total capital cost of Ferrator units installed.
Ferrator Chemical Feedstocks
Caustic Soda (50% concentration) (gal) | 3 | -- | -- | Ferrate solution produced (gal) | 4.5 |  | FTT estimated the reactant composition to produce ferrate is 3:0.5:1 of sodium hydroxide, ferric chloride, and sodium hypochlorite, with each at the indicated concentration in solution before mixing.
Ferric Chloride (40% concentration) (gal) | 0.5 | -- | -- | Ferrate solution produced (gal) | 4.5
Sodium Hypochlorite (13% concentration) (gal) | 1 | -- | -- | Ferrate solution produced (gal) | 4.5
Ferric Chloride Unit Cost ($) | 1.55 | -- | -- | Unit ferric chloride solution (gal) | 1 |  | Average cost for 40% ferric chloride from City of Boise proposal. Vendors included Kemira, BHSA, and Thatcher. EPA will update costs as data become available. (http://www.cityofboise.org/city_clerk/091112/12-240.pdf).
Scaling, Dosing, and Reductions
Number of Ferrators Required for Disinfection | 4 | -- | -- | Water produced (gal/day) | 100000000 |  | Estimated by FTT.
Number of Ferrators Required for Pre-treatment | 5 | -- | -- | Water produced (gal/day) | 100000000 |  | Estimated by FTT.
Number of Back-up Ferrators | 1 | -- | -- | -- | -- |  | Estimated by FTT.
Number of Ferrator Monitors | 2 | -- | -- | -- | -- |  | Estimated by FTT.
Pre-treatment Ferrate Dose (gal) | 3 | 1 | 5 | Unit water produced (gal) | 1000000 |  | Estimated by FTT.
Disinfection Ferrate Dose (gal) | 2 | 1 | 3 | Unit water produced (gal) | 1000000 |  | Estimated by FTT.
Ferric Chloride Solution (40% concentration) Dose for pH sedimentation (gal) | 0.075 | -- | -- | Unit water produced (gal) | 1000000 |  | FTT estimated that the FeCl3 dose is scalable linearly. Therefore, the pre-treatment dose is calculated linearly from the disinfection dose.
Ferric Chloride Solution (40% concentration) Dose for pH conditioning (gal) | 0.05 | -- | -- | Unit water produced (gal) | 1000000 |  | FTT estimated FeCl3 dose of 0.05 ppm for a ferrate disinfection dose of 2 ppm.
Reduction in Alum Required (%) | 100 | -- | -- | -- | -- |  | Alum is not required when using Ferrators.
Reduction in Flocculation Polymer (%) | 100 | -- | -- | -- | -- |  | Polymer is not required when using Ferrators.
Sludge Produced (lb) | 2.9962 | 0.43071 | 14.3568 | Unit water produced (ft3) | 1000 |  | Calculated using data from FTT and methodology from AWWA (2002). See Sludge Calculations worksheet for details.
Reduction in Lime Required (%) | 100 | -- | -- | -- | -- |  | Lime is not required when using Ferrators.
Reduction in Caustic Soda Required (%) | 100 | -- | -- | -- | -- |  | Caustic soda is not required when using Ferrators.
Reduction in Gaseous Chlorine Required (%) | 75 | -- | -- | -- | -- |  | FTT estimated chlorine dose is reduced by 75%. Chlorine only required to maintain residual in distribution system.
Conventional UV Unit Process Costs | [6 empty] | All data provided by Aquionics except where noted.
Capital Costs
UV Disinfection Units | 1 | -- | -- | Water produced (gal/day) | 3600000 | 45050 | Capital cost for one unit, which is required to treat 3.6 MGD.
Back-up UV Disinfection Units | 1 | -- | -- | -- | -- | 45050 | Capital cost for one unit, as a back-up.
Allen Bradley PLC & HMI Control Cabinet | 1 | -- | -- | UV Disinfection Unit | 1 | 90100 | Capital cost per unit.
Online UVT Monitor | 1 | -- | -- | System | 1 | 7500 | Capital cost per unit.
Ancillary Costs | 25% | -- | -- | UV Disinfection Unit | 1 |  | Ancillary capital cost estimated as 25% from AWWA (2008). This factor is applied to the UV unit cost and includes contingency, bonding, and mobilization.
UV System Lifetime (yr) | 20 | -- | -- | System | 1 | --
Utilities
Electricity (kWh/yr) | 210240 | -- | -- | Water produced (gal/day) | 3600000 | -- | Provided by Aquionics.
Replacement Parts
Lamps (quantity) | 6 | -- | -- | UV Disinfection Unit | 1 | 2700 | 6 lamps per unit, and $450 per lamp.
Quartz Sleeves (quantity) | 6 | -- | -- | UV Disinfection Unit | 1 | 420 | 1 quartz sleeve per lamp, and $70 per quartz sleeve.
Wiper Rings (quantity) | 6 | -- | -- | UV Disinfection Unit | 1 | 108 | 1 wiper ring per lamp, and $18 per wiper ring.
UV Sensors (quantity) | 6 | -- | -- | UV Disinfection Unit | 1 | 3000 | 1 sensor per lamp, and $500 per sensor.
Lamp Lifetime (yr) | 0.91324 | -- | -- | UV Disinfection Unit | 1 | --
Quartz Sleeves Lifetime (yr) | 5 | -- | -- | UV Disinfection Unit | 1 | --
Wiper Rings Lifetime (yr) | 2 | -- | -- | UV Disinfection Unit | 1 | --
UV Sensors Lifetime (yr) | 8 | -- | -- | UV Disinfection Unit | 1 | --
Scaling, Dosing, and Reductions
Reduction in Gaseous Chlorine Required (%) | 75 | -- | -- | -- | -- |  | Reduction in chlorine gas required not provided by vendor. Estimated that the reduction is equal to that for the Ferrator system to maintain a chlorine residual in distribution system.

## Unit Process Costs
| Base Quantity | Unit | Basis | Unit | Total Quantity | Unit | Total Annual Cost | Unit Cost | Unit | One Time Cost | Normalization for LCI ($/m3) | Unit Conversions |  | LCI Normalization Factor (Annual Dollars per Annual Volume of Water) |  | Use for LCI Normalization (Y/N)?
Base Case Processes | [11 empty] | gal/ft3 | 7.4805 | Water Produced at Surface Water Plant (gal) | 38747000000 | N
Source Water Acquisition | [11 empty] | gal/m3 | 264.17 | Total Water Delivered to Customers (gal) | 32641179385.5302 | Y
None
Flocculation
Alum | 0.962 | lb | 1000 | ft3 | 4982904.084 | lb | 888675 | 0.17834 | $/lb |  | 0.0071922
Polymer | 0.096 | lb | 1000 | ft3 | 497254.4616 | lb | 94000 | 0.18904 | $/lb |  | 0.00076076
Sedimentation
Wastewater Sludge | 3.5574 | lb | 1000 | ft3 | 18426310.4856 | lb | 15000 | 0.00081405 | $/lb |  | 0.0001214
Lime Addition
Lime | 0.177 | lb | 1000 | ft3 | 916812.9136 | lb | 53985 | 0.058883 | $/lb |  | 0.00043691
Sand Filtration
Sand Replacement | 0.428 | lb | 1000 | ft3 | 2216926.1413 | lb |  | 0 | $/lb |  | 0
Waste Sand Disposal | [6 empty] | 30000 |  |  |  | 0.00024279
GAC Adsorption
GAC Replacement | 0.156 | lb | 1000 | ft3 | 808038.5001 | lb | 1070955 | 1.3254 | $/lb |  | 0.0086674
GAC Regeneration
Natural Gas (purchased) (scf) | 75600000 | scf | 38747000000 | gal | 75600000 | scf | 428500.8 | 0.005668 | $/scf |  | 0.0034679
GAC NSF Cost | -- |  | -- |  | -- |  | 11500 | 0 |  |  | 9.3071e-05
Air Permit for GAC | -- |  | -- |  | -- |  | 4000 | 0 |  |  | 3.2373e-05
Conditioning
Caustic Soda | 1.073 | lb | 1000 | ft3 | 5557854.5552 | lb | 639756 | 0.11511 | $/lb |  | 0.0051776
Sodium Hexametaphosphate | 0.121 | lb | 1000 | ft3 | 626747.811 | lb | 258687 | 0.41274 | $/lb |  | 0.0020936
Disinfection
Gaseous Chlorine | 0.11 | lb | 1000 | ft3 | 569770.7373 | lb | 117926 | 0.20697 | $/lb |  | 0.00095439
Maintenance | -- |  | -- |  | -- |  | 10000 | 0 |  |  | 8.0932e-05
Risk Management Plan Cost | -- |  | -- |  | -- |  | 200 | 0 |  |  | 1.6186e-06
Fluorination
Hydrofluorosilicic Acid | 0.237 | lb | 1000 | ft3 | 1227596.9521 | lb | 364796 | 0.29716 | $/lb |  | 0.0029523
Distribution
Electricity | 76137689 | kWh | 38747000000 | gal | 76137689 | kWh | 2497316.1992 | 0.0328 | $/kWh |  | 0.020211
Sodium Hypochlorite | 0.023 | lb | 1000 | ft3 | 119133.8814 | lb | 10896 | 0.09146 | $/lb |  | 8.8183e-05
Facility-Wide Costs
Labor | 49 | worker | 38747000000 | gal | 49 | worker | 1822389.855 | 37191.6297 | $/worker |  | 0.014749
Maintenance (other than disinfection) | -- |  | -- |  | -- |  | 390000 | 0 |  |  | 0.0031563
Electricity (at plant) (purchased) | 39125286 | kWh | 38747000000 | gal | 39125286 | kWh | 1283309.3808 | 0.0328 | $/kWh |  | 0.010386
Electricity (at plant) (cogen) | 2287186 | kWh | 38747000000 | gal | 2287186 | kWh | 0 | 0 | $/kWh |  | 0
Base Case Total (w/ GAC) | [6 empty] | 9991892.235 |  |  |  | 0.080866
Base Case Total (w/o GAC) | [6 empty] | 8476936.435 |  |  |  | 0.068605
Ferrator Processes
Source Water Acquisition
None
Flocculation
Alum | 0 | lb | 1000 | ft3 | 0 | lb | 0 | 0.17834 | $/lb |  | 0
Polymer | 0 | lb | 1000 | ft3 | 0 | lb | 0 | 0.18904 | $/lb |  | 0
Ferrate | 3 | gal | 1000000 | gal | 116241 | gal | 113666.1162 | 0.97785 | $/gal |  | 0.00091992
Sedimentation
Ferric Chloride | 0.075 | gal | 1000000 | gal | 2906.025 | gal | 4504.3388 | 1.55 | $/gal |  | 3.6454e-05
Wastewater Sludge | 2.9962 | lb | 1000 | ft3 | 15519574.772 | lb | 12633.762 | 0.00081405 | $/lb |  | 0.00010225
Lime Addition
Lime | 0 | lb | 1000 | ft3 | 0 | lb | 0 | 0.058883 | $/lb |  | 0
Sand Filtration
Sand Replacement | 0.428 | lb | 1000 | ft3 | 2216926.1413 | lb |  | 0 | $/lb |  | 0
Waste Sand Disposal | [6 empty] | 30000 |  |  |  | 0.00024279
GAC Adsorption
GAC Replacement | 0.156 | lb | 1000 | ft3 | 808038.5001 | lb | 1070955 | 1.3254 | $/lb |  | 0.0086674
GAC Regeneration
Natural Gas (purchased) (scf) | 75600000 | scf | 38747000000 | gal | 75600000 | scf | 428500.8 | 0.005668 | $/scf |  | 0.0034679
GAC NSF Cost | -- |  | -- |  | -- |  | 11500 | 0 |  |  | 9.3071e-05
Air Permit for GAC | -- |  | -- |  | -- |  | 4000 | 0 |  |  | 3.2373e-05
Conditioning
Caustic Soda | 0 | lb | 1000 | ft3 | 0 | lb | 0 | 0.11511 | $/lb |  | 0
Ferric Chloride | 0.05 | gal | 1000000 | gal | 1937.35 | gal | 3002.8925 | 1.55 | $/gal |  | 2.4303e-05
Sodium Hexametaphosphate | 0.121 | lb | 1000 | ft3 | 626747.811 | lb | 258687 | 0.41274 | $/lb |  | 0.0020936
Disinfection
Gaseous Chlorine | 0.0275 | lb | 1000 | ft3 | 142442.6843 | lb | 29481.5 | 0.20697 | $/lb |  | 0.0002386
Maintenance | -- |  | -- |  | -- |  | 10000 | 0 |  |  | 8.0932e-05
Risk Management Plan Cost | -- |  | -- |  | -- |  | 200 | 0 |  |  | 1.6186e-06
Ferrate | 2 | gal | 1000000 | gal | 77494 | gal | 75777.4108 | 0.97785 | $/gal |  | 0.00061328
Electricity | 91250 | kWh | 6 | Unit | 167291.6667 | kWh | 5487.1667 | 0.0328 | $/kWh |  | 4.4408e-05
Incidental Repairs | 97200 | $ | 6 | Unit | 11 | Unit | 178200 |  |  |  | 0.0014422
Total Number of Ferrators and Capital Costs | 9 | Unit | 36500000000 | gal | 11 | Unit |  |  |  | 11177500 | 0
Ferrator Lifetime | 15 | yr | [8 empty] | 0
Bond Rate | 6% | % | [8 empty] | 0
Amortized Capital Cost | [6 empty] | 1150866.2941 |  |  |  | 0.0093141
Fluorination
Hydrofluorosilicic Acid | 0.237 | lb | 1000 | ft3 | 1227596.9521 | lb | 364796 | 0.29716 | $/lb |  | 0.0029523
Distribution
Electricity | 76137689 | kWh | 38747000000 | gal | 76137689 | kWh | 2497316.1992 | 0.0328 | $/kWh |  | 0.020211
Sodium Hypochlorite | 0.023 | lb | 1000 | ft3 | 119133.8814 | lb | 10896 | 0.09146 | $/lb |  | 8.8183e-05
Facility-Wide Costs
Labor | 49 | worker | 38747000000 | gal | 49 | worker | 1822389.855 | 37191.6297 | $/worker |  | 0.014749
Maintenance (other than Ferrators) | -- |  | -- |  | -- |  | 390000 | 0 |  |  | 0.0031563
Electricity (at plant, other than Ferrators) (purchased) | 39125286 | kWh | 38747000000 | gal | 39125286 | kWh | 1283309.3808 | 0.0328 | $/kWh |  | 0.010386
Electricity (at plant) (cogen) | 2287186 | kWh | 38747000000 | gal | 2287186 | kWh | 0 | 0 | $/kWh |  | 0
Ferrator Case Total (w/o GAC) | [6 empty] | 8241213.916 |  |  |  | 0.066697
Ferrator Case Total (w/ GAC) | [6 empty] | 9756169.716 |  |  |  | 0.078958
Conventional UV Processes
Source Water Acquisition
None
Flocculation
Alum | 0.962 | lb | 1000 | ft3 | 4982904.084 | lb | 888675 | 0.17834 | $/lb |  | 0.0071922
Polymer | 0.096 | lb | 1000 | ft3 | 497254.4616 | lb | 94000 | 0.18904 | $/lb |  | 0.00076076
Sedimentation
Wastewater Sludge | 3.5574 | lb | 1000 | ft3 | 18426310.4856 | lb | 15000 | 0.00081405 | $/lb |  | 0.0001214
Lime Addition
Lime | 0.177 | lb | 1000 | ft3 | 916812.9136 | lb | 53985 | 0.058883 | $/lb |  | 0.00043691
Sand Filtration
Sand Replacement | 0.428 | lb | 1000 | ft3 | 2216926.1413 | lb |  | 0 | $/lb |  | 0
Waste Sand Disposal | [6 empty] | 30000 |  |  |  | 0.00024279
GAC Adsorption
GAC Replacement | 0.156 | lb | 1000 | ft3 | 808038.5001 | lb | 1070955 | 1.3254 | $/lb |  | 0.0086674
GAC Regeneration
Natural Gas (purchased) (scf) | 75600000 | scf | 38747000000 | gal | 75600000 | scf | 428500.8 | 0.005668 | $/scf |  | 0.0034679
GAC NSF Cost | -- |  | -- |  | -- |  | 11500 | 0 |  |  | 9.3071e-05
Air Permit for GAC | -- |  | -- |  | -- |  | 4000 | 0 |  |  | 3.2373e-05
Conditioning
Caustic Soda | 1.073 | lb | 1000 | ft3 | 5557854.5552 | lb | 639756 | 0.11511 | $/lb |  | 0.0051776
Sodium Hexametaphosphate | 0.121 | lb | 1000 | ft3 | 626747.811 | lb | 258687 | 0.41274 | $/lb |  | 0.0020936
Disinfection
Gaseous Chlorine | 0.0275 | lb | 1000 | ft3 | 142442.6843 | lb | 29481.5 | 0.20697 | $/lb |  | 0.0002386
Maintenance | -- |  | -- |  | -- |  | 10000 | 0 |  |  | 8.0932e-05
Risk Management Plan Cost | -- |  | -- |  | -- |  | 200 | 0 |  |  | 1.6186e-06
UV System Electricity | 210240 | kWh/yr | 1314000000 | gal | 6199520 | kWh | 203344.256 | 0.0328 | $/kWh |  | 0.0016457
Lamps Replacement | 6 | Unit | 1314000000 | gal | 31 | Multiplier | 87885 |  |  | 1757700 | 0.00071127
Quartz Sleeves Replacement | 6 | Unit | 1314000000 | gal | 31 | Multiplier | 2604 |  |  | 52080 | 2.1075e-05
Wiper Rings Replacement | 6 | Unit | 1314000000 | gal | 31 | Multiplier | 1674 |  |  | 33480 | 1.3548e-05
UV Sensors Replacement | 6 | Unit | 1314000000 | gal | 31 | Multiplier | 9300 |  |  | 186000 | 7.5266e-05
Ancillary Capital Costs | 25% | % | 1 | Unit | 31 | Unit |  |  |  | 1049287.5
Total Number of UV Units and Capital Costs | 1 | Unit | 1314000000 | gal | 31 | Unit |  |  |  | 4197150 | 0
Bond Rate | 6% | % | [8 empty] | 0
Amortized Capital Cost | [6 empty] | 457408.3291 |  |  |  | 0.0037019
Fluorination
Hydrofluorosilicic Acid | 0.237 | lb | 1000 | ft3 | 1227596.9521 | lb | 364796 | 0.29716 | $/lb |  | 0.0029523
Distribution
Electricity | 76137689 | kWh | 38747000000 | gal | 76137689 | kWh | 2497316.1992 | 0.0328 | $/kWh |  | 0.020211
Sodium Hypochlorite | 0.023 | lb | 1000 | ft3 | 119133.8814 | lb | 10896 | 0.09146 | $/lb |  | 8.8183e-05
Facility-Wide Costs
Labor | 49 | worker | 38747000000 | gal | 49 | worker | 1822389.855 | 37191.6297 | $/worker |  | 0.014749
Maintenance (other than UV system parts) | -- |  | -- |  | -- |  | 390000 | 0 |  |  | 0.0031563
Electricity (at plant, other than UV system) (purchased) | 39125286 | kWh | 38747000000 | gal | 39125286 | kWh | 1283309.3808 | 0.0328 | $/kWh |  | 0.010386
Electricity (at plant) (cogen) | 2287186 | kWh | 38747000000 | gal | 2287186 | kWh | 0 | 0 | $/kWh |  | 0
Conventional UV Case Total | [6 empty] | 10665663.3201 |  |  |  | 0.086319

## Sludge Calculations
Unit Conversions
gal/ft3 | 7.4805
L/gal | 3.785
L/ft3 | 28.3137
mg/lb | 453592
lb/kg | 2.2046
mg/g | 1000
Suspended Solids Removed |  |  |  | Notes
| Average | Min | Max
Raw Water TSS (mg/L) | 43 | 1.9 | 225 | GCWW reported raw water TSS.
Finished Water TSS (mg/L) | 0 | 0 | 0 | GCWW reported finished water TSS.
TSS Removed (mg/L) | 43 | 1.9 | 225 | Calculated
TSS Removed (lb/1,000 ft3) | 2.6841 | 0.1186 | 14.0447 | Calculated
Base Case Mass of Sludge Produced per Water Treated | [7 empty] | Notes
| K (lb dry sludge / lb dry solid) | Concentration (lb/1,000 ft3) |  |  | Sludge (lb dry sludge / 1,000 ft3 water produced)
Contributions to Sludge |  | Average | Min | Max | Average | Min | Max
Alum Added | 0.44 | 0.962 | 0.682 | 1.351 | 0.42328 | 0.30008 | 0.59444 | K values and calculation methodology from Appendix E of AWWA (2002). Concentrations from GCWW base case data.
Polymer Added | 1 | 0.096 | 0.062 | 0.161 | 0.096 | 0.062 | 0.161
Lime Added | 2 | 0.177 | 0.046 | 0.291 | 0.354 | 0.092 | 0.582
Turbidity Removed | 1 | 2.6841 | 0.1186 | 14.0447 | 2.6841 | 0.1186 | 14.0447
Total Sludge Produced | -- | -- | -- | -- | 3.5574 | 0.57268 | 15.3822
Ferrate Mass of Sludge Produced per Water Treated |  |  |  | Notes
| Average | Min | Max
Raw Water TSS Removed (lb/1,000 ft3) | 2.6841 | 0.1186 | 14.0447 | GCWW TSS removed.
Ferrate TSS Produced (mg/L) | 5 | 5 | 5 | Per email from FTT.
Ferrate TSS Produced (lb/1,000 ft3) | 0.31211 | 0.31211 | 0.31211 | Calculated
Total Sludge Produced (lb/1,000 ft3) | 2.9962 | 0.43071 | 14.3568

## Chemical Unit Costs
Chemical Feedstocks | Unit Cost | Unit | Ferrate Costs | Quantity (gal) | Density (lb/gal) | Quantity (lb) | Cost ($) | Calculated Unit Cost ($/gal)
Alum | 0.17834 | $/lb | Caustic Soda | 3 | 8.3 | 24.9 | 2.8662 | --
Polymer | 0.18904 | $/lb | Ferric Chloride | 0.5 | 8.3 | 4.15 | 0.775 | --
Lime | 0.058883 | $/lb | Sodium Hypochlorite | 1 | 8.3 | 8.3 | 0.75912 | --
Caustic Soda | 0.11511 | $/lb | Ferrate Solution | 4.5 | 8.3 | 37.35 | 4.4003 | 0.97785
Sodium Hexametaphosphate | 0.41274 | $/lb
Gaseous Chlorine | 0.20697 | $/lb
Hydrofluorosilicic Acid | 0.29716 | $/lb
Sodium Hypochlorite | 0.09146 | $/lb
Ferric Chloride | 0.18675 | $/lb

## Cost Calculations
| GCWW Base Case 1 | GCWW Base Case 2 | Ferrate (w/GAC) | Ferrate (w/o GAC) | Conventional UV | Notes/Assumptions
Productivity Data
Total Finished Water Produced (gal) | 44396000000 | 44396000000 | 44396000000 | 44396000000 | 44396000000
Surface Water Plant Finished Water Produced (gal) | 38747000000 | 38747000000 | 38747000000 | 38747000000 | 38747000000
Percentage of Productivity due to Surface Water Plant (%) | 87.28% | 87.28% | 87.28% | 87.28% | 87.28%
Direct Residential Sales (surface water plant) (gal) | 15666020587.4403 | 15666020587.4403 | 15666020587.4403 | 15666020587.4403 | 15666020587.4403 | Computed percent from surface water plant used to allocate the water volume and revenues provided by GCWW for both plants to the surface water plant (Miller Plant).
Direct Non-residential Sales (surface water plant) (gal) | 11878247364.6274 | 11878247364.6274 | 11878247364.6274 | 11878247364.6274 | 11878247364.6274
Wholesale Sales (surface water plant) (gal) | 5096911433.4625 | 5096911433.4625 | 5096911433.4625 | 5096911433.4625 | 5096911433.4625
Water Losses (surface water plant) (gal) | 6105820614.4698 | 6105820614.4698 | 6105820614.4698 | 6105820614.4698 | 6105820614.4698
Water Losses (surface water plant) (%) | 15.76% | 15.76% | 15.76% | 15.76% | 15.76%
Revenues
Direct Residential Sales ($/yr) | 58038460.6721 | 58038460.6721 | 58038460.6721 | 58038460.6721 | 58038460.6721 | Computed percent from surface water plant used to allocate the water volume and revenues provided by GCWW for both plants to the surface water plant (Miller Plant).
Direct Non-residential Sales ($/yr) | 27142798.9008 | 27142798.9008 | 27142798.9008 | 27142798.9008 | 27142798.9008
Wholesale Sales ($/yr) | 13745951.2118 | 13745951.2118 | 13745951.2118 | 13745951.2118 | 13745951.2118
Fees/Other Revenues ($/yr) | 5096911.4335 | 5096911.4335 | 5096911.4335 | 5096911.4335 | 5096911.4335
Total Revenues ($/yr) | 104024122.2182 | 104024122.2182 | 104024122.2182 | 104024122.2182 | 104024122.2182
Unit Process Costs
Total Unit Process Costs (other than disinfection) | 6368066.9992 | 4853111.1992 | 4810458.1086 | 3295502.3086 | 6368066.9992
Disinfection Costs | 128126 | 128126 | 1450012.3716 | 1450012.3716 | 801897.0851
Facility-Wide Costs
Total Labor Costs | 1822389.855 | 1822389.855 | 1822389.855 | 1822389.855 | 1822389.855
Total Equipment Maintenance Costs (other than disinfection) | 390000 | 390000 | 390000 | 390000 | 390000
Plant Energy Costs (non-process specific) | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808
Bottom Line
Total Revenues ($/yr) | 104024122.2182 | 104024122.2182 | 104024122.2182 | 104024122.2182 | 104024122.2182
Total Costs ($/yr) | 9991892.235 | 8476936.435 | 9756169.716 | 8241213.916 | 10665663.3201
Total Water Sold (gal) | 32641179385.5302 | 32641179385.5302 | 32641179385.5302 | 32641179385.5302 | 32641179385.5302
Cost Increase from Baseline ($/yr) | -- | -- | -235722.519 | -1750678.319 | 673771.0851
Additional Revenue Needed to Offset Cost Rise ($/yr) | -- | -- |  |  | 673771.0851
Price Increase
Increase to Direct Residents Only ($/gal) | -- | -- | -- | -- | 4.3008e-05
Increase to Direct Residents and Non-residents Only ($/gal) | -- | -- | -- | -- | 2.4461e-05
Increase to All Customers (Direct and Wholesale) ($/gal) | -- | -- | -- | -- | 2.0642e-05
Base Case Price of Water ($/gal) | 0.0028475 | 0.0028475 | 0.0028475 | 0.0028475 | 0.0028475 | 2012 water price provided by GCWW.
Costs per Water Sold ($/gal) | 0.00030611 | 0.0002597 | 0.00029889 | 0.00025248 | 0.00032675
Costs as a Percent of Base Case Water Price (%) | 10.75% | 9.12% | 10.5% | 8.867% | 11.48%
New Price of Water to Offset Cost Rise ($/gal) | -- | -- | -- | -- | 0.0028681
Costs as a Percent of New Price of Water ($/gal) | -- | -- | -- | -- | 11.39%
Water Price Increase as a Percent of Base Case Water Price (%) | -- | -- | -- | -- | 0.7249%

## senseInfo (hidden)
selectionIndex | checkSelected | bookName | sheetName | cellAddress | rangeAddress | analysisString | minPercent | maxPercent | minValue | maxValue | baseValue | numIntervals | varyWhenStepping | isInput | groupCount | groupIndex | formulaIndex | ioIndex | [5 empty] | intIndex | intervalMode | useCellBase | tableRange
|  |  |  | #NAME? | [13 empty] | 9
senseTotal: | 4 | .
selectionIndex | checkSelected | bookName | sheetName | cellAddress | rangeAddress | analysisString | minPercent | maxPercent | minValue | maxValue | baseValue | numIntervals | varyWhenStepping | isInput | groupCount | groupIndex | formulaIndex | ioIndex | [5 empty] | intIndex | intervalMode | useCellBase | tableRange
1 | TRUE | 0 | Sensitivity Analysis | #NAME? | I23,I24,I25,I26 | Percentile: 1.00% to 99.00% |  |  |  |  | 3 | 7 | TRUE | TRUE | 4 | 0 | 1 | 4 | Pre-Treatment Ferrate Dose (ppm) | =RiskUniform(E23,F23,RiskName(B23),RiskStatic(C23)) | RiskUniform(E23,F23,RiskName(B23),RiskStatic(C23)) | 0 | 0 | 0 | 4 | TRUE |  | 1.00% | 5.00% | 25.00% | 50.00% | 75.00% | 95.00% | 99.00% | Perc%: 1% | Perc%: 5% | Perc%: 25% | Perc%: 50% | Perc%: 75% | Perc%: 95% | Perc%: 99%
2 | TRUE | 0 | Sensitivity Analysis | #NAME? | I23,I24,I25,I26 | Percentile: 1.00% to 99.00% |  |  |  |  | 2 | 7 | TRUE | TRUE | 4 | 1 | 1 | 5 | Disinfection Ferrate Dose (ppm) | =RiskUniform(E24,F24,RiskName(B24),RiskStatic(C24)) | RiskUniform(E24,F24,RiskName(B24),RiskStatic(C24)) | 0 | 0 | 0 | 4 | TRUE |  | 1.00% | 5.00% | 25.00% | 50.00% | 75.00% | 95.00% | 99.00% | Perc%: 1% | Perc%: 5% | Perc%: 25% | Perc%: 50% | Perc%: 75% | Perc%: 95% | Perc%: 99%
3 | TRUE | 0 | Sensitivity Analysis | #NAME? | I23,I24,I25,I26 | Percentile: 1.00% to 99.00% |  |  |  |  | 866000 | 7 | TRUE | TRUE | 4 | 2 | 1 | 6 | Ferrator Cost per Unit ($) | =RiskUniform(E25,F25,RiskName(B25),RiskStatic(C25)) | RiskUniform(E25,F25,RiskName(B25),RiskStatic(C25)) | 0 | 0 | 0 | 4 | TRUE |  | 1.00% | 5.00% | 25.00% | 50.00% | 75.00% | 95.00% | 99.00% | Perc%: 1% | Perc%: 5% | Perc%: 25% | Perc%: 50% | Perc%: 75% | Perc%: 95% | Perc%: 99%
4 | TRUE | 0 | Sensitivity Analysis | #NAME? | I23,I24,I25,I26 | Percentile: 1.00% to 99.00% |  |  |  |  | 0.06 | 7 | TRUE | TRUE | 4 | 3 | 1 | 7 | Bond Rate (%) | =RiskUniform(E26,F26,RiskName(B26),RiskStatic(C26)) | RiskUniform(E26,F26,RiskName(B26),RiskStatic(C26)) | 0 | 0 | 0 | 4 | TRUE |  | 1.00% | 5.00% | 25.00% | 50.00% | 75.00% | 95.00% | 99.00% | Perc%: 1% | Perc%: 5% | Perc%: 25% | Perc%: 50% | Perc%: 75% | Perc%: 95% | Perc%: 99%

## Sensitivity Analysis
| Deterministic Value | Distribution Type | Minimum Value | Maximum Value | Minimum Value % Change | Maximum Value % Change | @Risk Formula | Turn Stochastic Calculations On or Off
Base Case 1 (w/GAC) | [8 empty] | On
Inputs | [8 empty] | Off
Gaseous Chlorine Usage (lb/1,000 ft3) | 0.11 | Triangular | 0.08 | 0.161 | -27.27% | 46.36% | #NAME? | Off
Alum Usage (lb/1,000 ft3) | 0.962 | Triangular | 0.682 | 1.351 | -29.11% | 40.44% | #NAME? | Off
Lime Usage (lb/1,000 ft3) | 0.177 | Triangular | 0.046 | 0.291 | -74.01% | 64.41% | #NAME? | Off
Sodium Hypochlorite Usage (lb/1,000 ft3) | 0.023 | Triangular | 0.01 | 0.042 | -56.52% | 82.61% | #NAME? | Off
Natural Gas for GAC Regeneration Unit Cost ($/scf) | 0.005668 | Uniform | 0.0045344 | 0.0068016 | -20% | 20% | #NAME? | Off
Electricity (at plant) (purchased) (kWh) | 39125286 | Uniform | 35212757.4 | 43037814.6 | -10% | 10% | #NAME? | Off
Electricity (distribution) (purchased) (kWh) | 76137689 | Uniform | 68523920.1 | 83751457.9 | -10% | 10% | #NAME? | Off
Electricity Unit Cost ($/kWh) | 0.0328 | Uniform | 0.02624 | 0.03936 | -20% | 20% | #NAME? | Off
Results
Gaseous Chlorine Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Alum Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Lime Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Sodium Hypochlorite Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Natural Gas for GAC Regeneration Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Electricity (at plant) (purchased) Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Electricity (distribution) (purchased) Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Total Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Base Case 2 (w/o GAC)
Results
Gaseous Chlorine Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Distribution Electricity Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Electricity (at plant) (purchased) Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Total Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Ferrate (w/GAC)
Inputs
Pre-Treatment Ferrate Dose (ppm) | 3 | Uniform | 1 | 5 | -66.67% | 66.67% | #NAME? | Off
Disinfection Ferrate Dose (ppm) | 2 | Uniform | 1 | 3 | -50% | 50% | #NAME? | Off
Ferrator Cost per Unit ($) | 810000 | Uniform | 729000 | 891000 | -10% | 10% | #NAME? | Off
Bond Rate (%) | 6% | Uniform | 4% | 8% | -33.33% | 33.33% | #NAME? | Off
Results
Pre-Treatment Ferrate Cost ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Disinfection Ferrate Cost ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Ferrator Total Capital Cost ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Ferrator Amortized Capital Cost ($) | #NAME?
Total Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Ferrate (w/o GAC)
Results
Pre-Treatment Ferrate Cost ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Disinfection Ferrate Cost ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Ferrator Total Capital Cost ($) | #NAME?
Ferrator Amortized Capital Cost ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Total Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Conventional UV
Inputs
UV Electricity Usage to treat 3.6 MGD (kWh/yr) | 210240 | Uniform | 157680 | 262800 | -25% | 25% | #NAME? | Off
UV System Cost per Units needed to treat 3.6 MGD ($) | 45050 | Uniform | 40545 | 49555 | -10% | 10% | #NAME? | Off
Bond Rate (%) | 6% | Uniform | 4% | 8% | -33.33% | 33.33% | #NAME? | Off
Results
UV Electricity Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
UV Total Capital Cost ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
UV Amortized Capital Cost ($) | #NAME? | -- | -- | -- | -- | -- | -- | --
Total Costs ($) | #NAME? | -- | -- | -- | -- | -- | -- | --

## Results
Base Case Sensitivities
[6 empty] | Chlorine Usage Sensitivity Costs ($) |  |  |  | Chlorine Unit Cost Sensitivity Costs ($) |  |  |  | Electricity Usage Sensitivity Costs ($) |  |  |  | Electricity Unit Cost Sensitivity Costs ($) |  |  |  | Constants |  | Normalization Factor |  | Use for Normalization (Y/N)?
| Base Case Costs ($) |  | Ferrate Costs ($) |  | Conventional UV Costs ($) | Base Case 1 |  | Base Case 2 |  | Base Case 1 |  | Base Case 2 |  | Base Case 1 |  | Base Case 2 |  | Base Case 1 |  | Base Case 2 |  | gal/ft3 | 7.4805 | Water Produced at Surface Water Plant (gal) | 38747000000 | N
| Base Case 1 | Base Case 2 | Ferrate w/ GAC | Ferrate w/o GAC |  | 0.08 lb/1,000 ft3 | 0.161 lb/1,000 ft3 | 0.08 lb/1,000 ft3 | 0.161 lb/1,000 ft3 | -10% | +10% | -10% | +10% | -10% | +10% | -10% | +10% | -20% | +20% | -20% | +20% | gal/m3 | 264.17 | Total Water Delivered to Customers (gal) | 32641179385.5302 | Y
Source Water Acquisition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumping Energy, at Drinking Water Treatment Plant | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1283309.3808 | 1154978.4427 | 1411640.3189 | 1154978.4427 | 1411640.3189 | 1026647.5046 | 1539971.257 | 1026647.5046 | 1539971.257
Pre-Disinfection | 3495058.8 | 1980103 | 1937449.9094 | 422494.1094 | 3495058.8 | 3495058.8 | 3495058.8 | 1980103 | 1980103 | 3495058.8 | 3495058.8 | 1980103 | 1980103 | 3495058.8 | 3495058.8 | 1980103 | 1980103 | 3495058.8 | 3495058.8 | 1980103 | 1980103
Primary Disinfection | 128126 | 128126 | 1450012.3716 | 1450012.3716 | 801897.0851 | 95964.3636 | 182800.7818 | 95964.3636 | 182800.7818 | 116333.4 | 139918.6 | 116333.4 | 139918.6 | 128126 | 128126 | 128126 | 128126 | 128126 | 128126 | 128126 | 128126
Secondary Disinfection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2873008.1992 | 2373544.9594 | 3372471.439 | 2373544.9594 | 3372471.439
Overhead | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855 | 2212389.855
Total | 9991892.235 | 8476936.435 | 9756169.716 | 8241213.916 | 10665663.3201 | 9959730.5986 | 10046567.0168 | 8444774.7986 | 8531611.2168 | 9980099.635 | 10003684.835 | 8465143.835 | 8488729.035 | 9863561.2969 | 10120223.1731 | 8348605.4969 | 8605267.3731 | 9235767.119 | 10748017.351 | 7720811.319 | 9233061.551
Normalizations
[6 empty] | Chlorine Usage Sensitivity Costs ($/m3) |  |  |  | Chlorine Unit Cost Sensitivity Costs ($/m3) |  |  |  | Electricity Usage Sensitivity Costs ($/m3) |  |  |  | Electricity Unit Cost Sensitivity Costs ($/m3)
| Base Case Costs ($/m3) |  | Ferrate Costs ($/m3) |  | Conventional UV Costs ($/m3) | Base Case 1 |  | Base Case 2 |  | Base Case 1 |  | Base Case 2 |  | Base Case 1 |  | Base Case 2 |  | Base Case 1 |  | Base Case 2
| Base Case 1 | Base Case 2 | Ferrate w/ GAC | Ferrate w/o GAC |  | 0.08 lb/1,000 ft3 | 0.161 lb/1,000 ft3 | 0.08 lb/1,000 ft3 | 0.161 lb/1,000 ft3 | -10% | +10% | -10% | +10% | -10% | +10% | -10% | +10% | -20% | +20% | -20% | +20%
Source Water Acquisition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumping Energy, at Drinking Water Treatment Plant | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.010386 | 0.0093474 | 0.011425 | 0.0093474 | 0.011425 | 0.0083088 | 0.012463 | 0.0083088 | 0.012463
Pre-Disinfection | 0.028286 | 0.016025 | 0.01568 | 0.0034193 | 0.028286 | 0.028286 | 0.028286 | 0.016025 | 0.016025 | 0.028286 | 0.028286 | 0.016025 | 0.016025 | 0.028286 | 0.028286 | 0.016025 | 0.016025 | 0.028286 | 0.028286 | 0.016025 | 0.016025
Primary Disinfection | 0.0010369 | 0.0010369 | 0.011735 | 0.011735 | 0.0064899 | 0.00077665 | 0.0014794 | 0.00077665 | 0.0014794 | 0.0009415 | 0.0011324 | 0.0009415 | 0.0011324 | 0.0010369 | 0.0010369 | 0.0010369 | 0.0010369 | 0.0010369 | 0.0010369 | 0.0010369 | 0.0010369
Secondary Disinfection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.023252 | 0.019209 | 0.027294 | 0.019209 | 0.027294
Overhead | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905 | 0.017905
Total | 0.080866 | 0.068605 | 0.078958 | 0.066697 | 0.086319 | 0.080606 | 0.081308 | 0.068345 | 0.069048 | 0.08077 | 0.080961 | 0.06851 | 0.068701 | 0.079827 | 0.081904 | 0.067567 | 0.069644 | 0.074746 | 0.086985 | 0.062486 | 0.074725
Base Case 1 Total Cost ($/m3) | 0.080866
Percent of Base Case 1 Costs | [5 empty] | Percent of Base Case 1 Costs
| Base Case Costs (%) |  | Ferrate Costs (%) |  |  | Chlorine Usage Sensitivity Costs (%) |  |  |  | Chlorine Unit Cost Sensitivity Costs (%) |  |  |  | Electricity Usage Sensitivity Costs (%) |  |  |  | Electricity Unit Cost Sensitivity Costs (%)
[5 empty] | Conventional UV Costs (%) | Base Case 1 |  | Base Case 2 |  | Base Case 1 |  | Base Case 2 |  | Base Case 1 |  | Base Case 2 |  | Base Case 1 |  | Base Case 2
| Base Case 1 | Base Case 2 | Ferrate w/ GAC | Ferrate w/o GAC |  | 0.08 lb/1,000 ft3 | 0.161 lb/1,000 ft3 | 0.08 lb/1,000 ft3 | 0.161 lb/1,000 ft3 | -10% | +10% | -10% | +10% | -10% | +10% | -10% | +10% | -20% | +20% | -20% | +20%
Source Water Acquisition | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Pumping Energy, at Drinking Water Treatment Plant | 12.84% | 12.84% | 12.84% | 12.84% | 12.84% | 12.84% | 12.84% | 12.84% | 12.84% | 12.84% | 12.84% | 12.84% | 12.84% | 11.56% | 14.13% | 11.56% | 14.13% | 10.27% | 15.41% | 10.27% | 15.41%
Pre-Disinfection | 34.98% | 19.82% | 19.39% | 4.228% | 34.98% | 34.98% | 34.98% | 19.82% | 19.82% | 34.98% | 34.98% | 19.82% | 19.82% | 34.98% | 34.98% | 19.82% | 19.82% | 34.98% | 34.98% | 19.82% | 19.82%
Primary Disinfection | 1.282% | 1.282% | 14.51% | 14.51% | 8.025% | 0.9604% | 1.829% | 0.9604% | 1.829% | 1.164% | 1.4% | 1.164% | 1.4% | 1.282% | 1.282% | 1.282% | 1.282% | 1.282% | 1.282% | 1.282% | 1.282%
Secondary Disinfection | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Distribution | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 28.75% | 23.75% | 33.75% | 23.75% | 33.75%
Overhead | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14% | 22.14%

## Data Quality Information
QAPP Cost Data Quality Criteria
Criterion | Description | Base Case - DWT | Ferrate | Conventional UV
Current | Report time period of data. | Data is from GCWW for 2011. | Data is current as of the time of report preparation. | Data is current as of the time of report preparation.
Complete | All units are identified. Cost year reported. | Costs are for 2011. Units are identified. | Units are identified. | Units are identified.
Representative | Report if costs are for DWT or WWT unit processes. | DWT unit process information provided by GCWW. | Data provided by Ferrate Treatment Technologies, LLC. | Data provided by Aquionics.
Accurate/Reliable | Data source. Was data obtained directly from EPA partner? | DWT unit process information provided by GCWW. | Data provided by Ferrate Treatment Technologies, LLC. | Data provided by Aquionics.