## Cover
Life Cycle Inventory Development: AeMBR, District Scale, Treating Graywater (0.031 MGD)
Prepared by:
Ben Morelli and Sarah Cashman
Eastern Research Group
110 Hartwell Avenue
Lexington, MA 02421-3136
Last updated: 6/11/2019
*sarah.cashman@erg.com

## TOC
Table of Contents
| GPS-X Model | Exported GPS-X outputs
| LCI | Summary of LCI values developed in this workbook.
| LCC | Summary of life cycle costs used to compile the LCCA.
| Equalization | Calculation of LCI values for the equalization unit process.
| Fine Screen | Calculation of LCI values for the fine screen unit process.
| AeMBR | Calculation of LCI values for the AeMBR unit process.
| UV | Calculation of LCI values for the UV disinfection unit process.
| Chlorine | Calculation of LCI values for the chlorination unit process.
| Sources | Documents sources used in workbook.
Hidden | Conversion Factors | Documents conversion factors used in workbook calculations.

## GPS-X Model
GPS-X Model Documentation
Originally linked to excel file of GPS-X Model Output. Saved as static values in final workbook version.
| Unit | Parameter | Value | Units
| Influent | Flow | 117.3477 | m3/d
| Influent | TSS | 93.287 | mg/L
| Influent | VSS | 43.8449 | mg/L
| Influent | VSS/TSS | 0.47 | -
| Influent | cBOD5 | 165 | mg/L
| Influent | COD | 330 | mg/L
| Influent | BOD/COD | 0.58
| Influent | Soluble COD | 151.8 | mg/L
| Influent | Ammonia N | 1.9 | mgN/L
| Influent | TKN | 8.5 | mgN/L
| Influent | TN | 9.14 | mgN/L
| Influent | Soluble PO4-P | 0.5 | mgP/L
| Influent | TP | 1.12 | mgP/L
| Influent | Total Alkalinity | 284.7868 | mgCaCO3/L
| Influent | pH | 6.9999 | -
| Influent | BOD/cBOD | 1.16 | -
| Influent | BOD | 191.4 | mg/L
| Influent | TOC | 106 | mgC/L
| Influent | BOD/TOC | 1.8057 | -
| Influent | sCOD/COD | 0.46 | -
| Equalization Tank | HRT | 8.6308
| Equalization Tank | Volume | 42.2 | [m3]
| Equalization Tank | Tank Depth | 3.6 | [m]
| Fine Screen | Solids TSS | 60000 | mg/L
| Fine Screen | Solids Capture | 7.0101 | %
| Fine Screen | Solids Disposed | 0.7674 | kg/d
| AeMBR | Tank Volume | 24.4 | m3
| AeMBR | MLSS | 10529.9143 | mg/L
| AeMBR | MLVSS | 4630.1422 | mg/L
| AeMBR | Influent TKN | 8.39 | mg N/L
| AeMBR | Influent BOD | 160 | mg/L
| AeMBR | Soluble COD | 19.4885 | mg/L
| AeMBR | Ammonia N | 0.18854 | mgN/L
| AeMBR | Nitrite N | 0.12199 | mgN/L
| AeMBR | Nitrate N | 0.045965 | mgN/L
| AeMBR | Soluble PO4-P | 0.11594 | mgP/L
| AeMBR | HRT | 4.3792 | h
| AeMBR | DO | 1.999 | mgO2/L
| AeMBR | Trans-Mem. Pressure | 2.2722 | kPa
| AeMBR | WAS Flow | 0.9759 | m3/d
| AeMBR | WAS Production | 10.2641 | kg/d
| AeMBR | Solids Disposal | 0.01279 | m3/d
| AeMBR | Biological Air Flow | 30.0578 | m3/h
| AeMBR | Cleaning Air Flow | 55 | m3/h
| AeMBR | Biological Air Flow | 35.34% | Percent of total airflow
| AeMBR | Cleaning Air Flow | 64.66% | Percent of total airflow
| AeMBR | Permeate Flow | 117.5872 | m3/day
| UV | Influent TSS | 0.84239 | mg/L
| UV | COD | 18.66 | mg/L
| UV | Ammonia N | 0.18854 | mgN/L
| UV | Nitrite N | 0.12199 | mgN/L
| UV | Nitrate N | 0.045965 | mgN/L
| UV | TKN | 0.8236 | mgN/L
| UV | TN | 0.99155 | mgN/L
| UV | Soluble PO4-P | 0.11594 | mgP/L
| UV | TP | 0.19599 | mgP/L
| UV | UV Contact Time | 0.10042 | min
| UV | UV Dose | 30.668 | (mW-s/cm2)
| UV | Eff. Coliform Density | 3.7926 | MPN/100mL
| Chlorination | Influent Ammonia | 0.18854 | mgN/L
| Chlorination | Influent TOC | 6.01 | [gC/m3]
| Chlorination | Detention Time | 48.9849 | min
| Chlorination | Chlorine Dosage | 3.0035 | mg/L
| Chlorination | Free Residual | 1.0004 | mg/L
| Chlorination | Total Residual | 1.0004 | mg/L
| Chlorination | Total Trihalomethane | 7.915 | ppb
| Chlorination | Eff. Coliform Density | 4.0557e-06 | MPN/100mL
| Chlorination | sTOC | 5.72 | [gC/m3]
| Chlorination | UV254/sCOD | 0.001 | [1/(COD.cm)]
| Chlorination | Soluble Inert COD | 14 | [mgCOD/L]
| Effluent | Flow | 117.5872 | m3/d
| Effluent | TSS | 0.84239 | mg/L
| Effluent | VSS | 0.37041 | mg/L
| Effluent | cBOD5 | 2.8254 | mg/L
| Effluent | BOD5 | 3.2775 | mg/L
| Effluent | COD | 18.66 | mg/L
| Effluent | Ammonia N | 0.05 | mgN/L
| Effluent | Nitrite N | 0.12199 | mgN/L
| Effluent | Nitrate N | 0.045965 | mgN/L
| Effluent | TKN | 0.8236 | mgN/L
| Effluent | TN | 0.99155 | mgN/L
| Effluent | Soluble PO4-P | 0.11594 | mgP/L
| Effluent | TP | 0.19599 | mgP/L
Energy Usage Summary
|  | Aeration Power | Pumping Power | Mixing Power | Heating Power | Other Power | Total Power
| Equalization (out) | 31.67 | 0 | 0 | 0 | 0 | 31.67
| Fine Screen (xscreeneff) | 0 | 0.11 | 0 | 0 | 96.43 | 96.54
| AeMBR (ovf) | 11990.32 | 22.37 | 0 | 0 | 0 | 12012.68
| Filter Press (filtrate) | 0 | 0.13 | 0 | 0 | 19285.22 | 19285.35
| UV (eff) | 0 | 0 | 0 | 0 | 2454.48 | 2454.48
| Layout Total | 12021.98 | 22.61 | 0 | 0 | 21836.13 | 33880.72
copied out of GPS-X

## LCI
Life Cycle Inventory Data Summary
LCI
| Unit Process | Input/Output | Description | Quantity | Quantity Units | Lifespan | Annual Quantity | Quantity per m3
| Fine Screen | Electricity | Operation Energy | 3202.3558 | kWh | 1 | 3202.3558 | 0.074714
| Fine Screen | Screening Disposal | Screening Disposal | 174.6505 | kg | 1 | 174.6505 | 0.0040748
| Fine Screen | Steel | Screen | 444 | kg | 15 | 29.6 | 0.0006906
| Equalization | Concrete | Tank | 19.1905 | m3 | 40 | 0.47976 | 1.1193e-05
| Equalization | Steel | Tank | 1144.4473 | kg | 40 | 28.6112 | 0.00066753
| Equalization | Electricity | Mixing and Aeration | 4071.8768 | kWh | 1 | 4071.8768 | 0.095001
| Chlorination | Concrete | Contact Basin | 40 | m3 | 40 | 1 | 2.3331e-05
| Chlorination | Steel | Contact Basin Rebar | 10 | kg | 40 | 0.25 | 5.8328e-06
| Chlorination | Electricity | Chlorine pumping/injection | 1788.264 | kwh | 1 | 1788.264 | 0.041722
| Chlorination | Sodium Hypochlorite | Chlorination | 138.411 | kg NaOCl | 1 | 138.411 | 0.0032293
| AeMBR | Concrete | Basin | 33.9871 | m3 | 40 | 0.84968 | 1.9824e-05
| AeMBR | Steel | Rebar | 2024.7886 | kg | 40 | 50.6197 | 0.001181
| AeMBR | Polyvinyl Fluoride | Membrane | 253.6536 | kg | 10 | 25.3654 | 0.0005918
| AeMBR | Sodium Hypochlorite | Membrane Cleaning | 30.8268 | kg | 1 | 30.8268 | 0.00071922
| AeMBR | Electricity | MBR Operation | 18831.8481 | kwh | 1 | 18831.8481 | 0.43937
| AeMBR | Methane | Process Emissions | 205.7341 | kg | 1 | 205.7341 | 0.0048
| AeMBR | N2O | Process Emissions | 2.1474 | kg | 1 | 2.1474 | 5.01e-05
| AeMBR | Sludge Disposal | to Central WWTP | 356.4476 | m3 | 1 | 356.4476 | 0.0083163
| UV | Electricity | UV system | 1227.24 | kWh | 1 | 1227.24 | 0.028633
| UV | Steel | UV system | 32.6587 | kg | 30 | 1.0886 | 2.5399e-05
| Storage | HDPE | Tank | 1594.8327 | kg | 40 | 39.8708 | 0.00093023

## LCC
Life Cycle Costs
AeMBR - District Scale, Graywater
| LCCA Value | Cost Category | Quantity | Quantity Units | Value | Value Units | Cost | Cost Units | Lifespan | Cost Source | Lifespan Reference | Note
| AeMBR | Annual, Energy | 18831.8481 | kWh/year | 0.19371 | $/kWh | 3648.0115 | $/yr | 1 |  | n.a.
| Equalization | Floating Aerator/Mixer | 2 | units/installation | 18386.8116 | $/unit | 36773.6231 | $/lifespan | 20 | CAPDET | CAPDET, mechanical aerator
| Equalization | Direct Cost | n.a. | n.a. | n.a. | n.a. | 16548.1304 | $/lifespan | n.a.
| Equalization | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 27194.0943 | $/lifespan | n.a.
| Equalization | Concrete material | 19.1905 | m3/tank | 258 | $/m3 | 4951.155 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Installation | 19.1905 | m3/tank | 397.88 | $/m3 | 7635.5254 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Rebar material | 1.8774 | short tons/installation | 983 | $/short ton | 1845.4589 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Installation | 1.8774 | short tons/installation | 1374 | $/short ton | 2579.5122 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Forms | 653.9607 | ft2/installation | 2 | $/ft2 | 1307.9215 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Form Installation | 653.9607 | ft2/installation | 2.55 | $/ft2 | 1667.5999 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Direct Cost | n.a. | n.a. | n.a. | n.a. | 8994.2278 | $/lifespan | n.a.
| Equalization | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 14780.5144 | $/lifespan | n.a.
| Equalization | Annual, Energy | 4071.8768 | kWh/year | 0.19371 | $/kWh | 788.7836 | $/lifespan
| Fine Screen | Annual, Energy | 3202.3558 | kWh/year | 0.19371 | $/kWh | 620.3444 | $/yr | 1 |  | n.a.
| Fine Screen | Equipment & Installation | 2 | Units per Installation | 18174.5787 | $/unit | 36349.1574 | $/installation | 15 | CAPDET | CAPDET, Process Equipment
| Fine Screen | Direct Cost | n.a. | n.a. | n.a. | n.a. | 16357.1208 | $/lifespan
| Fine Screen | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 26880.2019 | $/lifespan
| AeMBR | Blowers | 2 | units/installation | 5012.7738 | $/unit | 10025.5477 | $/lifespan | 15 | CAPDET | CAPDET, Process Equipment
| AeMBR | Blower Installation | n.a. | n.a. | 100% |  | 10025.5477 | $/lifespan
| AeMBR | Membrane System | 366.7118 | m2 | 79.6622 | $/m2 | 29213.0541 | $/lifespan | 10 | CAPDET | CAPDET, membrane
| AeMBR | Permeate Pumps | 6 | units/installation | 1734 | $/pump | 10404 | $/lifespan | 25 | CAPDET | CAPDET, Pumps
| AeMBR | Pump Installation | n.a. | n.a. | 150% |  | 15606 | $/lifespan
| AeMBR | Sludge Pumps | 2 | units/installation | 62853% | $/pump | 1257.0501 | $/lifespan
| AeMBR | Sludge Pump Install | n.a. | n.a. | 150% |  | 1885.5752 | $/lifespan
| AeMBR | Fine Diffusers | 21 | units/installation | 58.8014 | $/unit | 1234.8292 | $/lifespan | 10 | CAPDET | CAPDET, Diffuser
| AeMBR | Coarse Diffusers | 7 | units/installation | 35.4836 | $/unit | 248.3852 | $/lifespan | 10 | CAPDET | CAPDET, Diffuser
| AeMBR | Diffuser System | 3 | units/installation | 16223 | $/unit | 48669 | $/lifespan | 20 | CAPDET | CAPDET, swing arm diffuser
| AeMBR | Air Distribution Ancillary Cost | n.a. | n.a. | 10% | capital cost | 5015.2214 | $/lifespan
| AeMBR | Installation | 75 | labor hours | 50 | $/hour | 3750 | $/lifespan
| AeMBR | Air Piping | n.a. | n.a. | n.a. | n.a. | 7627.1772 | $/lifespan | 40 | CAPDET | CAPDET, Structural
| AeMBR | Concrete material | 33.9871 | m3/tank | 258 | $/m3 | 8768.6613 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AeMBR | Installation | 33.9871 | m3/tank | 397.88 | $/m3 | 13522.7712 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AeMBR | Rebar material | 2.2319 | short tons/installation | 983 | $/short ton | 2194.0016 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AeMBR | Installation | 2.2319 | short tons/installation | 1374 | $/short ton | 3066.692 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AeMBR | Forms | 875.5 | ft2/installation | 2 | $/ft2 | 1751.0001 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AeMBR | Form Installation | 875.5 | ft2/installation | 2.55 | $/ft2 | 2232.5251 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AeMBR | Minor Costs | n.a. | n.a. | 10% | of TBCC | 17649.7039 | $/lifespan
| AeMBR | Direct Cost | n.a. | n.a. | n.a. | n.a. | 87366.0343 | $/lifespan
| AeMBR | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 143571.5164 | $/lifespan
| AeMBR | Sodium hypochlorite | 205.5118 | kg/yr | 2 | $/kg | 411.0236 | $/yr
| Chlorinator | Capital, Pumps and Injector | 1 | equipment | 46300.9901 | $/lifespan | 46300.9901 | $/lifespan | 25 | U.S. EPA 2002 | CAPDET, Pumps
| Chlorinator | Direct Cost | n.a. | n.a. | n.a. | n.a. | 20835.4455 | $/lifespan | n.a.
| Chlorinator | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 34239.5822 | $/lifespan | n.a.
| Chlorinator | Concrete material | 4.1091 | m3/tank | 258 | $/m3 | 1060.1472 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Installation | 4.1091 | m3/tank | 397.88 | $/m3 | 1634.9278 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Rebar material | 0.11295 | short tons/installation | 983 | $/short ton | 111.0326 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Installation | 0.11295 | short tons/installation | 1374 | $/short ton | 155.1972 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Forms | 87.5751 | ft2/installation | 2 | $/ft2 | 175.1501 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Form Installation | 87.5751 | ft2/installation | 2.55 | $/ft2 | 223.3164 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Basin Direct Cost | n.a. | n.a. | n.a. | n.a. | 1511.8971 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Basin Indirect Cost | n.a. | n.a. | n.a. | n.a. | 2484.551 | $/lifespan | n.a.
| Chlorinator | Annual, Energy | 1788.264 | kWh/year | 0.19371 | $/kWh | 346.4136 | $/yr | n.a.
| Chlorinator | Sodium hypochlorite | 922.7401 | kg/yr | 2 | $/kg | 1845.4802 | $/yr
| UV Unit (40 GPM) | Capital, Purchased Equipment | 2 | UV Unit | 2596 | $/unit | 5192 | $/lifespan | 30 | Manufacturer Website | CAPDET UV structural
| UV Unit (40 GPM) | UV Installation | n.a. | n.a. | 100% | of equipment cost | 5192 | $/lifespan
| UV Unit (40 GPM) | Direct Cost | n.a. | n.a. | n.a. | n.a. | 4672.8 | $/lifespan
| UV Unit (40 GPM) | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 7678.968 | $/lifespan
| UV Unit (40 GPM) | Annual, Material | 2 | bulb | 240 | $/unit | 480 | $/lifespan | 1.3699 | Manufacturer Website | CAPDET, lamps
| UV Unit (40 GPM) | Annual, Material | 2 | quartz sleeve | 114 | $/unit | 228 | $/lifespan | 5 | Manufacturer Website | CAPDET, quartz sleeves
| UV Unit (40 GPM) | Annual, Electricity | 1227.24 | kWh/year | 0.19371 | $/kWh | 237.7348 | $/yr | n.a.
| Treated Effluent Storage | Capital, Purchased Equipment | 4 | tanks | 2000 | $/unit | 8000 | $/lifespan | 40 | CAPDET | CAPDET, structural
| Treated Effluent Storage | Tank Installation | n.a. | n.a. | 100% | of equipment cost | 8000 | $/lifespan
| Treated Effluent Storage | Direct Cost | n.a. | n.a. | n.a. | n.a. | 7200 | $/lifespan | n.a.
| Treated Effluent Storage | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 11832 | $/lifespan | n.a.
[6 empty] | Capital Costs | 804054.3336
| Cost year | Description | Value | Units | Source |  |  | Direct Cost Elements | Direct Cost Factor
| 2016 | Membrane System Cost | 7.4009 | $/ft2 | Hydromantis 2014 |  |  | Mobilization | 0.05
| 2014 | Standard 550 scfm Swing Arm Diffuser | 16000 | $ | Hydromantis 2014 |  |  | Site Preparation | 0.07
| 2014 | Standard 3000 gpm Pump and Driver Unit | 20500 | $ | Hydromantis 2014 |  |  | Site Electrical | 0.15
[8 empty] | Yard Piping | 0.1
[8 empty] | Instrumentation and Control | 0.08
[8 empty] | Lab and Administration Building | n.a.
[8 empty] | Indirect Cost Elements | Indirect Cost Factor
[8 empty] | Miscellaneous Costs | 0.05
[8 empty] | Legal Costs | 0.02
[8 empty] | Engineering Design Fee | 0.15
[8 empty] | Inspection Costs | 0.02
[8 empty] | Contingency | 0.1
[8 empty] | Technical | 0.02
[8 empty] | Profit | 0.15
Hydromantis 2014

## Equalization
Equalization |  |  |  | LCI Quantity
|  | Parameter | Value | Units | Note/Source
|  | Flowrate | 1291.6667 | Gallons per Hour (GPH) | calculated
|  | Volume of Equalization Tank | 11160 |  | CAPDET Method
|  | Dimension (square) | 11.4265 | ft | assumed
|  | Volume of Equalization Tank | 11160.1867 | gallons | calculated
|  | Volume of Equalization Tank | 42.2459 | m3 | GPS-X input, calculated
| Hour | Percent of Daily Flow | Gallons per hour | Cumulative Flow (gal) | FLOW difference | Avg. Flow Accumulation (gal)
| 0 | 1% | 310 | 310 | 981.6667 | 1291.6667
| 1 | 1% | 310 | 620 | 981.6667 | 2583.3333
| 2 | 1% | 310 | 930 | 981.6667 | 3875
| 3 | 1% | 310 | 1240 | 981.6667 | 5166.6667
| 4 | 1% | 310 | 1550 | 981.6667 | 6458.3333
| 5 | 3% | 930 | 2480 | 361.6667 | 7750
| 6 | 11% | 3410 | 5890 | -2118.3333 | 9041.6667
| 7 | 15% | 4650 | 10540 | -3358.3333 | 10333.3333
| 8 | 11% | 3410 | 13950 | -2118.3333 | 11625
| 9 | 11% | 3410 | 17360 | -2118.3333 | 12916.6667
| 10 | 8% | 2480 | 19840 | -1188.3333 | 14208.3333
| 11 | 3% | 930 | 20770 | 361.6667 | 15500
| 12 | 3% | 930 | 21700 | 361.6667 | 16791.6667
| 13 | 2% | 620 | 22320 | 671.6667 | 18083.3333
| 14 | 2% | 620 | 22940 | 671.6667 | 19375
| 15 | 2% | 620 | 23560 | 671.6667 | 20666.6667
| 16 | 3% | 930 | 24490 | 361.6667 | 21958.3333
| 17 | 3% | 930 | 25420 | 361.6667 | 23250
| 18 | 4% | 1240 | 26660 | 51.6667 | 24541.6667
| 19 | 4% | 1240 | 27900 | 51.6667 | 25833.3333
| 20 | 5% | 1550 | 29450 | -258.3333 | 27125
| 21 | 3% | 930 | 30380 | 361.6667 | 28416.6667
| 22 | 1% | 310 | 30690 | 981.6667 | 29708.3333
| 23 | 1% | 310 | 31000 | 981.6667 | 31000
31000
Aeration Energy Estimate
|  | O2 = | 1.3961 | lb/hr
|  | STE | 5 | lb O2/hp-hr
|  | O2 Transfer Waste/O2 transfer water | 0.9 | fraction
|  | Oxygen Requirement | 15 | mg/L/hour
|  | O2 saturation | 8.6 | mg/L @ 23*C
|  | OTE | 2.8731
|  | Aeration Horsepower | 0.48593 | HP
|  | Specified Horsepower | 0.60741 | HP
|  | Motor Efficiency | 0.877 | Harris et al. 1982
|  | Aeration Energy | 4071.8768 | kWh
* Motors Operate 90% of the time
Equalization Basin Construction
|  | Average Wetted Volume | 42.2459 | m3
|  | Wall Height | 4.0924 | m
|  | Wall Length | 3.7115 | m
|  | Wall Thickness | 0.22866 | m (9 inches)
|  | Top/Bottom thickness | 0.30488 | m (12 inches)
|  | Slab Length | 4.1688 | m
|  | Slab Width | 4.1688 | m
|  | Wall Count | 4 | count
|  | Slab Count | 1 | count
|  | Wall A Area | 60.755 | m2
|  | Wall A Volume | 13.8921 | m3
|  | Bottom Volume | 5.2984 | m3
|  | Total Concrete Volume | 19.1905 | m3
|  | Concrete Density | 2300 | kg/m3
|  | Tank Lifespan | 40 | years
|  | Concrete Mass | 9450.9248 | kg
|  | Rebar spacing | 0.3048 | m (center on center)
|  | Rebar Length | 512.6881 | m
|  | rebar weight | 1144.4473 | kg

## Fine Screen
Fine Screening |  |  | LCI Quantity
| Screenings | 10.3108 | ft3/year
| Screenings | 174.6505 | kg/year
| Unit Mass1 | 444 | kg
1 Two units
Energy Requirement, Screening
| Electricity | 3202.3558 | kwh/yr
Energy Calculation from Harris (1982)
Screening Generation and Disposal
| Plant Location | Screenings Generation (ft3/Mgal)
| Uniontown, PA | 0.9
| East Hartford, CT | 1.33
| Duluth, MN | 0.56
| Lamberts Point WWCP, VA | 1.2
| Village Creek WWTP, TX | 0.72
| County of Milwaukee, WI | 0.6
| Twin Cities Metro, MN | 1.15
| Chicago, IL | 0.83
| Average | 0.91125
from U.S. EPA 2003
| Ratio between mixed WW/Graywater TSS | 0.42727
Used to scale graywater screenings

## AeMBR
AeMBR, District Scale, Treating Graywater |  |  | LCI Quantity
| Flowrate | 0.031 | MGD
| Flowrate | 117.3478 | m3/day
| Flowrate | 42861.2713 | m3/year
AeMBR Design and Operational Parameters
| Parameter | Value | Units | Note
| SRT | 15 | days | Range is 10-30 days
| HRT | 5 | hours | Yoon 2016
| Biological SOTE | 2% | per foot submergence | Tarallo et al. 2015
| Cross-flow SOTE | 0.75% | per foot submergence | Sanitaire 2014
| Tank Depth | 2.98 | m | calculated
| Length | 3.37 | m | calculated
| Width | 2.43 | m | calculated
| Diffuser Height | 0.3 | m | above floor
| Biological SOTE | 0.17585 | fraction | total
| Cross-flow SOTE | 0.065945 | fraction | total
| Backflush Flux | 40 | LMH | Yoon 2016
| Constant Flux | 20 | LMH | Cashman and Mosley 2016
| Backflush Flow | 4325.5834 | gpd | calculated, 45 second backflush every 10 minutes.
| Scour Air Demand | 0.225 | Nm3/m2/hr | Average of CAPDET Default and GE Eco-aeration.
| Membrane Area, Necessary | 244.4745 | m2 | calculated based on flow rate and flux
| Membrane Area, Installed | 366.7118 | m2 | Reserve capacity = 50% of treatment capacity
| Cross Flow Air | 1320.1624 | m3/day | calculated
| DO Setpoint | 2 | mgO2/L | range 1-2
| Tank Volume | 24.4475 | m3/day | includes both membrane and aeration area (submerged)
| Graywater - AeMBR | [Virus] | [protozoa] | [Bacteria]
| LRT Target | 6 | 4.5 | 3.5
| Technology | Log Reduction | Log Reduction | Log Reduction | Associated Dose | Dose Units | Log Reduction Source
| Membrane bioreactor | 5 | 5 | 5 | n/a | n/a | Sharvelle et al. 2017
| Advanced Oxidation, Ozone | 0 | 0 | 0 | - | - | -
| UV | 0 | 4 | 2 | 30 | mj/cm2 | Sharvelle et al. 2017
| Chlorination | 4 | 0 | 4 | 32 | mg-min/L free chlorine (CT) | Sharvelle et al. 2017
| Total LRV | 9 | 9 | 11
Sodium Hypochlorite
| Parameter | Value | Units | Note/Source
| Sodium Hypolchlorite Use | 950 | L/cassette | 950L of 12.5% NaOCl is required for cleaning 1, 48 module membrane cassette (GE Power & Water, 2014)
| Surface area per cassette | 1649.9596 | m2/cassette | 370 ft2/module, 48 modules per cassette (GE Power & Water, 2014)
| Sodium Hypolchlorite Use | 0.57577 | L/m2/yr | calculated
| Density of 12.5% wt NaOCl | 1.168 | kg/L
| Annual NaOCl, 15% solution (ecoinvent) | 30.8268 | kg/year | calculated, converts 12.5% solution to 15% solution (for ecoinvent)
Sludge
| Parameter | Value | Units | Note/Source
| Flow | 1.1295e-05 | m3/sec | GPS-X output
| Head | 3.048 | meters | assumed
| Pump Efficiency | 0.6 | - | standard pump efficiency (Tarallo et al. 2015)
| Gravity | 9.81 | m/s2
| Energy | 0.00078805 | kW | calculated
| Hours of Operation | 8760 | hours | assumed continuous
| Energy Use | 6.9033 | kWh | calculated
*Assumes s.g. of 1.4 and continuous pumping
Permeate Pump Energy Calculation
| Parameter | Value | Units | Note/Source
| Flow | 0.0015505 | m3/sec | GPS-X output
| Head | 13.716 | meters | GE Z-MOD L Packaged LeapMBR plant
| Pump Efficiency | 0.6 | - | standard pump efficiency (Tarallo et al. 2015)
| Gravity | 9.81 | m/s2
| Energy | 0.3477 | kW | calculated
| Hours of Operation | 8760 | hours | assumed
| Energy Use | 3045.8952 | kWh | calculated
Miscellaneous Energy Use
| Energy Use | 3766.3696 | kWh per year
*25% of aeration, permeate pumping and sludge pumping energy.
Martin et al. 2011 report surveyed MBR energy consumption of 0.6-1.2 kWh/m3 for MBRs operating at HRTs of <12 hours.
Krzeminski et al. 2012 reports a range of between 0.5 and 0.7 kWh/m3 for membrane related modules.
Cornel and Krause 2004 report a range of 1-2 kWh/m3 (refers to full system)
Tank Storage
|  | Tank Volume | 5000 | gallon
|  | Tank Quantity | 4 | count
|  | Tank Mass | 398.7082 | kg
|  | Total tank mass | 1594.8327 | kg
Tank Depot Website
Unit Construction
| Average Wetted Volume | 36.6712 | m3
| Wall Height | 3.5898 | m
| Wall A Length | 4.589 | m
| Wall B Length | 3.37 | m |  | Train 1
| Wall Thickness | 0.31467 | m (1.0 ft)
| Top/Bottom thickness | 0.45732 | m (1.5 ft)
| Slab Length | 3.9993 | m |  | Train 2
| Slab Width | 4.589 | m
| Wall A Count | 2 | count
| Wall B Count | 4 | count (includes internal partition) |  | Train 3
| Top/Bottom Count | 1 | count
| Wall A Area | 32.9468 | m2
| Wall B Area | 48.3899 | m2
| Wall A Volume | 10.3673 | m3
| Wall B Volume | 15.2267 | m3
| Bottom Volume | 8.3931 | m3
| Total Concrete Volume | 33.9871 | m3
| Concrete Density | 2300 | kg/m3
| Tank Lifespan | 40 | years
| Concrete Mass | 9450.9248 | kg
| Rebar spacing | 0.3048 | m (center on center)
| Rebar Length | 1308.263 | m
| rebar weight | 2024.7886 | kg
Diffuser Quantity Estimation
| Combined Airflow | 50.0632
| Blower Capacity per tank | 57.5726
| Installed Blower Capacity | 115.1453 | scfm
| Required Biological Airflow | 17.6913 | scfm
| Required Scour Airflow | 32.3718 | scfm
| Fine Bubble, fraction of airflow | 35.34%
| Coarse Bubble, fraction of airflow | 64.66%
| Fine Bubble Diffusers (2 scfm) | 20.3451
| Coarse Bubble Diffusers (12 scfm) | 6.2046
| Installed Fine Bubble Diffusers (2 scfm) | 21
| Installed Coarse Bubble Diffusers (12 scfm) | 7
Calculation of PVDF Mass in Membranes
Specifications for GE ZeeWeed 500D Modules and Cassettes
ZeeWeed 500D
|  | Membrane Material | PVDF
|  | Nominal Pore Size | 0.04 | µm
|  | Membrane outer diameter | 0.0019 | m
|  | Membrane inner diameter | 0.0008 | m
|  | Module nominal membrane surface area | 31.6 | m2
|  | Module height | 2.198 | m
|  | Module width | 0.844 | m
|  | Module depth | 0.049 | m
Note: Does not subtract volume of pores
|  | Membrane surface area (m2) | 366.7118
|  | Circumference of fiber (m) | 0.005969
|  | Length of fiber required to equal membrane surface area (m) | 61435.7793
|  | Cross-sectional area of fiber (m2) | 2.3326e-06
|  | Total fiber volume (m3) | 0.14331
|  | Density PVDF (g/cm3) | 1.77
|  | Mass of PVDF in 1 cassette (kg) | 253.6536
Greenhouse Gas Emission Calculations
Proposed EF
| System Level | Influent TKN to reactor (mg/L) | Influent Flow to reactor (MGD) | Influent TKN to reactor (g/yr) | % Emitted as N2O1 | Source | Basis for N2O EF selection | kg N2O/yr | kg N2O/m3 | Influent BOD (mg/L) | MCF | kg CH4/yr | kg CH4/m3
| Aerobic MBR | 8.39 | 0.031 | 359606.066 | 0.38% | Chandran 2012 | Plug Flow Aerobic Reactors | 2.1474 | 5.01e-05 | 160 | 0.05 | 205.7341 | 0.0048
1 Based on N2O emissions factors of four plug-flow aerobic treatment processes from Chandran (2012). No data for CSTR reactors is available.
2 Methane Correction Factor is assumed equal to the midpoint of the uncertainty range, 0 to 0.1, for a well-managed aerobic treatment plant (IPCC 2006).
Wall A
Wall B
Note on C141: Author: 1000 kg/m3 = 1g/cm3

## UV
UV Dose Calculations |  |  | LCI Quantity
Sheet Description: The calculations presented on this sheet relate nominal bulb intensity to the delivered UV intensity and dosage. Dosages (in mJ/cm2) relate directly to target log reductions. Delivered UV intensity is determined by wastewater transmittance, bulb sleeve transmittance, lamp UV output, and a lamp aging factor. Dosage is calculated as the product of delivered UV intensity and the duration of UV exposure (in seconds). UV chamber diameter is fixed at 5 inches. Chamber length can be altered to meet a specific UV dose target. Regardless of the necessary LRT a minimum UV dosage of 30 mj/mc2 is applied whenever this technology is utilized (BGLUMR 2013).
User Input Values
LCI Quantity
Unit Note: mW*sec/cm2 = mJ/cm2
| Parameter | Value | Units | Note
| Flowrate | 0.031 | MGD | scenario value
| Flowrate | 1.3582 | liters per second | calculated
| Flowrate | 21.5278 | gpm | Equalization tank allows for treatment of a consistent flowrate
| UV Chamber Length | 51 | in | user specified
| UV Chamber Diameter | 5 | in | based on commercial unit size
| Volume | 0.0082049 | m3 | calculated
*based on 50% of unit volume for40 gpm unit
Calculate delivered UV lamp intensity from nominal intensity*
| Parameter | Value | Units | Note
| Target design dose | 30 | mJ/cm2 | see link
| Transmittance (x%) | 0.79 | low value for microfiltration effluent | Tchobanoglous et al. 2014
| Flowrate (Q) | 117.3478 | m3/day | scenario value
| Quartz sleeve transmittance (Ft) | 0.85 | unitless | fraction of lamp UV output transmitted through quartz sleeve
| Aging Factor (Fp) | 0.7 | unitless | output may be reduced by 30% after 7000 hours of use
| Lamp % UV output | 85% |  | UV output of low-pressure high intensity lamps can be modulated between 30 and 100% (Tchobanoglous et al. 2014, pg 1385)
| Intensity | 4.9311 | mW/cm2 | delivered intensity
| Nominal Intensity | 9.75 | mW/cm2 | 8-15 mW/cm2
| Time | 6.041 | seconds | duration of UV exposure (reasonable range 2-21 seconds (Qasim 1999))
| Calculated Dose | 29.7886 | mJ/cm2 | should be close to 'Target design dose'
Electricity Consumption
| Parameter | Value | Units | Note/Source
| Power | 0.14 | kW | Atlantic Ultraviolet 2007 for 40 GPM unit
| Hours per year | 8766 | hours
| Electricity Consumption | 1227.24 | kWh
| Electricity Consumption | 0.028633 | kWh/m3
Infrastructure
| Unit Mass | 32.6587 | kg | Atlantic Ultraviolet 2007 for 40 GPM unit, mass of 2 units

## Chlorine
Chlorination
Sheet Description: The calculations presented on this sheet estimate target chlorine residuals and conctact times (CT) based on free chlorine dosage (mg/L), instantaneous demand, and chlorine decay. A targeted free chlorine residual of 1 mg/L was selected based on the recommended range of 0.5-2.5 mg/L. Instantaneous demand of both TOC and Ammonia is calculated. Given the residual requirement and a standard contact time of 30 minutes achieving 4-log reduction of bacterial and viral pathogens does not lead to significant increases in chemical dosage. No log reduction of protozoa is assumed to occur.
Current Study:
| Flowrate | 0.031 | MGD |  |  | User Input Values
| Flowrate | 117.3478 | m3/day |  |  | LCI Quantity
| Volume of Cl disinfection tank | 2.45 | m3
| HRT | 30.0645 | minutes (15 is minimum BGLUMR 2014)
Determining Chlorine Dosage:
1. Determine initial chlorine demand of Ammonia present in treated wastewater
2. Calculate the allowance needed to account for chlorine decay
3. Select target free chlorine residual
Free Chlorine Calculations:
| Estimated Dose (as available Cl) | 3.0755 | mg/L
| Target Residual Achieved based on above dosage | 0.99746 | mg/L free chlorine
| NaOCl Solution Strength | 15% | sodium hypochlorite by wt
| NaOCl , 15%, Solution Strength | 14.29% | available chlorine by wt
| Associated NaOCl Dosage (mg/L) | 21.5285 | mg NaOCl, 15% solution/L
| Annual NaOCl Requirement | 138.411 | kg NaOCl, 15% solution (in ecoinvent)
| Chlorine Requirement | 0.79566 | lb Cl/day
1 definition of relationship between wt NaOCl and free chlorine
| 1. Insatantaneous TOC demand |  |  | 0.49964 | mgCl2/L
| 1. NH4+-N concentration |  |  | 0.18854 | mgN/L | At a pH of 7.5 and temperature of 30 °C, about 97.5% of ammonia exists in water as ammonium. I assume that as NH4+ reacts with HOCl that the small amount of NH3 converts to NH4+ so that, in the end, NH4+-N concentration is about equal to the NH3-N concentration. | (Canadian Council of Ministers of the Environment, 2010)
| Breakpoint ratio |  |  | 7.6 | mg Cl2/ mg NH4+-N (Tchobanoglous et al. 2014)
| Cl2 dose to reach breakpoint |  |  | 1.9326 | mgCl2/L
| 2. Chlorine Decay |  |  | 0.14546 | mgCl2/L
| 3. Free chlorine concentration |  |  | 1 | mgCl2/L
| Total Cl2 dosage |  |  | 3.078 | mgCl2/L
| CT (based on free chlorine) |  |  | 32.0029 | mg-min/L
Instantaneous demand of TOC
| A1 | 0.62
| A2 | 0.522
| A3 | 0.302
| A4 | 0.842
| Cl dose | 3.0775 | Total Cl2 Dose (enter manually)
| soluble inert COD | 14 | GPS-X output
| TOC | 6.01 | GPS-X output
| sTOC | 5.72 | GPS-X output
| UV254/sCOD | 0.001 | GPS-X output
| UV254 | 0.014 | calculated UV absorbance at 254nm
| Clinst | 0.49964 | mgCL2/L
*Calculation method from GPS-X technical reference
Estimate Chlorine Decay
*Excludes instantaneous demand
| Chlorine decay constant | 0.41667 | GPS-X
| time (min) | t10 (hr) | Dose (mg Cl2/L) | Available (mg Cl2/L)
| 1 | 0.011667 | 1.1429 | 1.1374
| 2 | 0.023333 | 1.1429 | 1.1319
| 3 | 0.035 | 1.1429 | 1.1265
| 4 | 0.046667 | 1.1429 | 1.1211
| 5 | 0.058333 | 1.1429 | 1.1158
| 6 | 0.07 | 1.1429 | 1.1105
| 7 | 0.081667 | 1.1429 | 1.1053
| 8 | 0.093333 | 1.1429 | 1.1001
| 9 | 0.105 | 1.1429 | 1.095
| 10 | 0.11667 | 1.1429 | 1.0899
| 11 | 0.12833 | 1.1429 | 1.0849
| 12 | 0.14 | 1.1429 | 1.0799
| 13 | 0.15167 | 1.1429 | 1.075
| 14 | 0.16333 | 1.1429 | 1.0701
| 15 | 0.175 | 1.1429 | 1.0653
| 16 | 0.18667 | 1.1429 | 1.0604
| 17 | 0.19833 | 1.1429 | 1.0557
| 18 | 0.21 | 1.1429 | 1.051
| 19 | 0.22167 | 1.1429 | 1.0463
| 20 | 0.23333 | 1.1429 | 1.0417
| 21 | 0.245 | 1.1429 | 1.0371
| 22 | 0.25667 | 1.1429 | 1.0325
| 23 | 0.26833 | 1.1429 | 1.028
| 24 | 0.28 | 1.1429 | 1.0235
| 25 | 0.29167 | 1.1429 | 1.0191
| 26 | 0.30333 | 1.1429 | 1.0147
| 27 | 0.315 | 1.1429 | 1.0103
| 28 | 0.32667 | 1.1429 | 1.006
| 29 | 0.33833 | 1.1429 | 1.0017
| 30 | 0.35 | 1.1429 | 0.99746 | Should equal the target residual
Contact Basin
| Average Wetted Volume | 3.4069 | m3
| Total Volume | 7.5381 | m3
| Short Wall Height | 0.91463 | m
| Short Wall Length | 1.9309 | m
| Long Wall Height | 0.91463 | m
| Long Wall Length | 4.2683 | m
| Wall Thickness | 0.10163 | m (4 inches)
| Top/Bottom thickness | 0.15244 | m (6 inches)
| Top/Bottom Length | 4.2683 | m
| Top/Bottom Width | 2.1341 | m
| Long Wall Count | 2 | count
| Short Wall Count | 3 | count (includes internal partition)
| Top/Bottom Count | 2 | count
| Wall area | 87.5751 | ft2
| Short Wall Volume | 0.53843 | m3
| Long Wall Volume | 0.79348 | m3
| Top/Bottom Volume | 2.7772 | m3
| Total Concrete Volume | 4.1091 | m3
| Concrete Density | 2300 | kg/m3
| Tank Lifespan | 40 | years
| Concrete Mass | 9450.9248 | kg
| Rebar spacing | 0.3048 | m (center on center)
| Rebar Length | 102.7702 | m
| rebar weight | 102.4692 | kg
| Pipe Lifespan | 50 | years
| Piping Length | 10 | m
| Pipe weight | 12.3518 | kg
for linked calculations see RVFW Workbook
| Current | 1.7 | Amp
| Draw | 120 | Volt
| Power (continuous) | 0.204 | kW
| Electricity Use | 1788.264 | kWh/year
| Electricity Use | 0.051771 | kWh/m3
based on power requirements of Stenner Peristaltic, Chemical Feed Pump (assuming liquid NaOCl solution, i.e. not generated onsite)
for linked calculations see RVFW Workbook

## Sources
Sources
| General Information |  |  | Additional information
No | Name | Description | Category | Doi | Text reference | Year
1 | Atlantic Ultraviolet 2007 |  |  |  | Atlantic Ultraviolet. 2007. Sanitron Ultraviolet Water Purifiers. https://www.freshwatersystems.com/specifications/sanitronfamilyinfo.pdf. Accessed 2/6/2018
2 | BGLUMR 2014 |  |  |  | (BGLUMR) Board, G. L.-U. M. R. Recommended Standards for Wastewater Facilities; 2014.
3 | Brake 2007 |  |  |  | Brake, P. A Bug’s-Eye-View of the BOD Test; 2007.
4 | Cashman and Mosley 2016 |  |  |  | Cashman, S.; Mosley, J. Life Cycle Assessment and Cost Analysis of Water and Wastewater Treatment Options for Sustainability: Influence of Scale on Membrane Bioreactor Systems; Cincinnati, OH, 2016.
5 | Chandran 2012 |  |  |  | Chandran, K. 2012. Greenhouse Nitrogen Emissions from Wastewater Treatment Operation: Phase I. Water Environment Research Foundation.
6 | Cornel and Krause 2004 |  |  |  | Cornel, P.; Krause, S. State of the Art of MBR in Europe. Tech. Note Natl. Inst. L. Infrastruct. Manag. 2004, 151–162.
7 | GE Power & Water 2014 |  |  |  | GE Power & Water. Z-MOD L Packaged Plants: MBR Platform Systems Featuring LEAPmbr Technology. General Electric 2014.
8 | Harris et al. 1982 |  |  |  | Harris, R.W.; Cullinane, M. J.; Sun, P. T. Process Design and Cost Estimating Algorithms for the Computer Assisted Procedure for Design and Evaluation of Wastewater Treatment Systems (CAPDET); U.S. Environmental Protection Agency PB82-190455; U.S. Environmental Protection Agency: Washington, D.C., 1982; p 1700.
9 | Hiltunen et al. 2002 |  |  |  | Hiltunen, T., Summers, P. & Robinson, R. B. Small Public Water System Technology Guide Volume II: (2002). Available at: http://www.unh.edu/wttac/WTTAC_Water_Tech_Guide_Vol2/.
10 | Hydromantis 2014 |  |  |  | Hydromantis. CAPDETWorks Version 3.0 Software: Rapid Design and Costing Solution for Wastewater Treatment Plants. (2014).
11 | Impero and Hammler 2015 |  |  |  | Impero, J. & Hammler, K. MBR Screening Part 2: Selecting an MBR screen. the MBR site (2015). Available at: http://www.thembrsite.com/features/mbr-screening-part-2-selecting-an-mbr-screen/.
12 | IPCC 2006 |  |  |  | IPCC. 2006. IPCC Guidelines for National Greenhouse Gas Inventories. Edited by Simon Eggleston, Leandro Buendia, Kyoko Miwa, Todd Ngara, and Kiyoto Tanabe. IGES, Japan: Intergovernmental Panel on Climate Change, National Greenhouse Gas Inventories Programme.
13 | Krzeminski et al. 2012 |  |  |  | Krzeminski, P.; van der Graff, J. H.; van Lier, J. B. Specific Energy Consumption of Membrane Bioreactor (MBR) for Sewage Treatment. Water Sci. Technol. 2012, 65 (2), 380–392.
14 | Martin et al. 2011 |  |  |  | Martin, I.; Pidou, M.; Soares, A.; Judd, S.; Jefferson, B. Modelling the Energy Demands of Aerobic and Anaerobic Membrane Bioreactors for Wastewater Treatment. Environ. Technol. 2011, 32 (9), 921–932.
15 | Pirnie et al. 2006 |  |  |  | Pirnie, M., Linden, K. G. & Malley, J. P. J. Ultraviolet disinfection guidance manual for the final long term 2 enhanced surface water treatment rule. 2, (2006).
16 | Qasim 1999 |  |  |  | Qasim, S. R. Wastewater Treatment Plants: Planning, Design, and Operation, 2nd ed.; CRC Press, 1999.
17 | Sanitaire 2014 |  |  |  | Sanitaire. Aeration Systems and Efficient Oxygen Transfer. (2014).
18 | Sharvelle et al. 2017 |  |  |  | Sharvelle, S.; Ashbolt, N.; Clerico, E.; Hultquist, R.; Leverenz, H.; Olivieri, A. Risk-Based Framework for the Development of Public Health Guidance for Decentralized Non-Potable Water Systems; 2017.
19 | Tarallo et al. 2015 |  |  |  | Tarallo, S.; Shaw, A.; Kohl, P.; Eschborn, R. A Guide to Net-Zero Energy Solutions for Water Resource Recovery Facilities; WERF ENER1C12; IWA Publishing: London, UK, 2015; p 440.
20 | Tchobanoglous et al. 2014 |  |  |  | Tchobanoglous, G. et al. Wastewater Engineering: Treatment and Resource Recovery. (McGraw-Hill Education, 2014).
21 | U.S. EPA 2003 |  |  |  | U.S. EPA. Wastewater Technology Fact Sheet, Screening and Grit Removal. (2003).
22 | Yoon 2016 |  |  |  | Yoon, S.-H. (2016). HRT and SRT - OnlineMBR. Retrieved December 1, 2017, from http://onlinembr.info/hrt-and-srt/
23 | Yoon 2016 |  |  |  | Yoon, S.-H. Membrane Bioreactor Processes. (CRC Press, 2016).

## Conversion Factors (hidden)
Conversion Factors, Project Constants, and Looksups used throughout workbook
Conversion Factors
| Category | Parameter | Value | Unit | Source
| Area | sqft/m2 | 10.7639
| Area | ft2/acre | 43560
| Area | ft2/m2 | 10.7639
| Cost | $/kW CHP ICE Capital Cost | 1600 | $/kW | Wiser et al. 2010
| Cost | Maintenance Costs CHP ICE | 0.025 | $/kWh | Wiser et al. 2010
| Density | Water Density | 999.97 | kg/m³
| Density | biogas Density | 1.214 | kg/m3
| Density | Methane Density | 0.656 | kg/m3
| Density | Compost Density | 453.5929 | kg/m3
| Density | water density | 8.338 | lb/gal @ 60*F
| Density | Ferric Chloride | 1.37 | s.g. | http://edwardschemicals.com/MSDS/water-treatment/FERRIC%20CHLORIDE%2038%20-%2042.pdf
| Density | water density | 8.329 | lb/g at 70*F | http://www.engineeringtoolbox.com/water-specific-volume-weight-d_661.html
| Distance | m/mile | 1609.34
| Distance | ft/m | 3.2808
| Distance | km/mile | 1.6093
| Energy | HHV to LHV, generic | 0.9 |  | https://www.csemag.com/single-article/understanding-cogeneration-systems/f4ee71595545969c02674b7b029620a1.html?tx_ttnews%5BsViewPointer%5D=1
| Energy | BTU/Dekatherm (DTH) | 1000000
| Energy | MJ/kWh | 3.6
| Energy | Btu/ft3 | 1027
| Energy | BTU/MJ | 947.817 |  | google conversions
| Energy | 1 MCF = | 1000 | ft3 of natural gas
| Energy | kW/HP | 0.7457
| Generic | g/kg, ml/L, etc… | 1000
| Infrastructure | Handrail | 2.7216 | kg/ft
| Volume | gal/3 | 264.1721
| Volume | ft3/m3 | 35.3147
| Volume | gallons/ft3 | 7.4805
| Volume | L/gallon | 3.7854
| Volume | m3/yd3 | 0.76455
| Volume | L/m3 | 1000
| Wastewater Characteristics | BOD/cBOD ratio | 1.16 |  | Source: Brake 2007
| Weight | lb/kg | 2.2046
| Weight | kg per short ton | 907.1847
| Weight | kg/mg | 1e-06
| Time | days per year | 365.25
| Time | hours per year | 8760 |  | google conversions
| TIme | minutes per hour | 60
| Time | hours per day | 24
| Food Waste, raw, before processing |  | 650 | kg/m3 | EC 2013
| Density of diesel |  | 0.832 | kg/L | MIT Energy Conversions
| Density of solids, wastewater |  | 1400 | kg/m3
| Density of water |  | 1000 | kg/m3
| Food Waste, air filled pore space |  | 48.1% | v/v | Sundberg et al. 2011
| Sodium Hypochlorite s.g. | 1.211 | s.g. @68*F | JCI Jones Chem Sheet
| N to N2O |  | 1.5714 |  | stoichiometry
| kg CH4/kg BOD | theoretical maximum production | 0.6
| Rebar |  |  |  |  | Steel Grating
|  | Rod Size | Rod Weight |  |  | Bar Size Inches: | Weight Per Sq. Ft: | Sect. Prop. Ft. of Width:
| Rod Number | (in) | (lb per linear foot) | kg/ft | kg/m | 3/4 x 3/16 | 5.67 | Sx=0.194 / 1x=0.73
| 2 | 0.250 = 1/4" | 0.17 | 0.077111 | 0.25299 | 1 x 1/8 | 5.15 | Sx=0.228 / 1x=0.114
| 3 | 0.375 = 3/8" | 0.38 | 0.17237 | 0.5655 | 1 x 3/16 | 7.35 | Sx=0.344 / 1x=0.171
| 4 | 0.500 = 1/2" | 0.67 | 0.30391 | 0.99707 | 1-1/4 x 1/8 | 6.2 | Sx=0.358 / 1x=0.223
| 5 | 0.625 = 5/8" | 1.04 | 0.47174 | 1.5477 | 1-1/4 x 3/16 | 9.03 | Sx=0.536 / 1x=0.335
| 6 | 0.750 = 3/4" | 1.5 | 0.68039 | 2.2322 | 1-1/2 x 1/8 | 7.35 | Sx=0.515 / 1x=0.387
| 7 | 0.875 = 7/8" | 2.04 | 0.92533 | 3.0359 | 1-1/2 x 3/16 | 10.94 | Sx=0.773 / 1x=0.579
| 8 | 1.000 = 1" | 2.67 | 1.2111 | 3.9734 | 1-3/4 x 3/16 | 12.62 | Sx=1.052 / 1x=0.902
| 9 | 1.128 = 1 1/8" | 3.4 | 1.5422 | 5.0598 | 2 x 3/16 | 14.3 | Sx=1.375 / 1x=1.375
| 10 | 1.270 = 1 1/4" | 4.3 | 1.9504 | 6.3991 | 2-1/4 x 3/16 | 15.87 | Sx=1.740 / 1x=1.958
| 11 | 1.410 = 1 3/8" | 5.31 | 2.4086 | 7.9022 | 2-1/2 x 3/16 | 17.55 | Sx=2.148 / 1x=2.685
| 14 | 1.693 = 1 3/4" | 7.65 | 3.47 | 11.3845 | http://www.directmetals.com/dm/products/bar-grating/carbon-steel-bar-grating.html
| 18 | 2.257 = 2 1/4" | 13.6 | 6.1689 | 20.2391
Pipe Weights
| material/inner diameter | Wt/ft | Unit | Wall thickness | Source
| concrete27 | 322 | lb/ft |  | http://www.theturnerco.com/products/reinforced-concrete-pipe
| metal18 | 93.54 | lb/ft | 0.5 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal8 | 27.73 | lb/ft | 0.312 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal12 | 49.61 | lb/ft | 0.375 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal4 | 11.36 | lb/ft | 0.25 | http://www.saginawpipe.com/steel_pipe.htm#pipechart1
| metal10 | 41.59 | lb/ft | 0.375 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal3 | 8.69 | lb/ft | 0.25 | http://www.saginawpipe.com/steel_pipe.htm#pipechart1
| concrete24 | 265 | lb/ft |  | http://www.theturnerco.com/products/reinforced-concrete-pipe
| metal6 | 21.06 | lb/ft | 0.312 | http://www.saginawpipe.com/steel_pipe.htm#pipechart1
| PVC6 | 3.733 | lb/ft | 0.28 | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC4 | 2.118 | lb/ft | 0.237 | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
GREET Fuel Heating Values
| Fuels |  | Lower Heating Value (LHV) [1] |  |  | Higher Heating Value (HHV) [1] |  |  | Density
| Gaseous Fuels @ 32 F and 1 atm |  | Btu/ft3 [2] | Btu/lb [3] | MJ/kg [4] | Btu/ft3 [2] | Btu/lb [3] | MJ/kg [4] | grams/ft3
| Natural gas |  | 983 | 20267.2259 | 47.1413 | 1089 | 22452.705 | 52.2247 | 22
| Hydrogen |  | 290 | 51682.0289 | 120.2116 | 343 | 61127.3652 | 142.1814 | 2.5452
| Still gas (in refineries) |  | 1458 | 20162.6287 | 46.898 | 1584 | 21905.078 | 50.9509 | 32.8
| Liquid Fuels |  | Btu/gal [2] | Btu/lb [3] | MJ/kg [4] | Btu/gal [2] | Btu/lb [3] | MJ/kg [4] | grams/gal
| Crude oil |  | 129670 | 18351.6428 | 42.6857 | 138350 | 19580.0863 | 45.543 | 3205
| Conventional gasoline |  | 116090 | 18679.4122 | 43.448 | 124340 | 20006.875 | 46.5357 | 2819
| Reformulated or low-sulfur gasoline |  | 113601.5098 | 18210.6734 | 42.3578 | 121848.3804 | 19532.6723 | 45.4327 | 2829.5773
| CA reformulated gasoline |  | 113927.154 | 18271.8133 | 42.5 | 122174.4341 | 19594.5248 | 45.5766 | 2828.1932
| U.S. conventional diesel |  | 128450 | 18397.1063 | 42.7914 | 137380 | 19676.0954 | 45.7663 | 3167
| Low-sulfur diesel |  | 129487.8476 | 18320.1475 | 42.6124 | 138490 | 19593.7864 | 45.5749 | 3206
| Petroleum naphtha |  | 116920 | 19320.1249 | 44.9383 | 125080 | 20668.5017 | 48.0746 | 2745
| NG-based FT naphtha |  | 111520 | 19081.2361 | 44.3827 | 119740 | 20487.6902 | 47.6541 | 2651
| Residual oil |  | 140352.5222 | 16967.6174 | 39.4664 | 150110 | 18147.2268 | 42.2102 | 3752
| Methanol |  | 57250 | 8638.7317 | 20.0936 | 65200 | 9838.346 | 22.8838 | 3006
| Ethanol |  | 76330 | 11587.1903 | 26.9516 | 84530 | 12831.9822 | 29.847 | 2988
| Butanol |  | 99837 | 14774.8988 | 34.3662 | 108458 | 16050.7224 | 37.3337 | 3065
| Acetone |  | 83127 | 12721.1795 | 29.5893 | 89511 | 13698.1425 | 31.8617 | 2964
| E-Diesel Additives |  | 116090 | 18679.4122 | 43.448 | 124340 | 20006.875 | 46.5357 | 2819
| Liquefied petroleum gas (LPG) |  | 84950 | 20037.6862 | 46.6074 | 91410 | 21561.4466 | 50.1516 | 1923
| Liquefied natural gas (LNG) |  | 74720 | 20908.2324 | 48.6322 | 84820 | 23734.4255 | 55.2059 | 1621
| Dimethyl ether (DME) |  | 68930 | 12416.9812 | 28.8817 | 75610 | 13620.3097 | 31.6806 | 2518
| Dimethoxy methane (DMM) |  | 72200 | 10061.1975 | 23.4022 | 79196.8954 | 11036.2273 | 25.6701 | 3255
| Methyl ester (biodiesel, BD) |  | 119550 | 16134.0924 | 37.5277 | 127960 | 17269.0796 | 40.1676 | 3361
| Fischer-Tropsch diesel (FTD) |  | 123670 | 18593.1307 | 43.2473 | 130030 | 19549.3231 | 45.4714 | 3017
| Renewable Diesel I (SuperCetane) |  | 117059 | 18729.0271 | 43.5634 | 125294 | 20046.598 | 46.6281 | 2835
| Renewable Diesel II (UOP-HDO) |  | 122887 | 18907.8407 | 43.9794 | 130817 | 20127.9793 | 46.8174 | 2948
| Renewable Gasoline |  | 115983 | 18589.6569 | 43.2393 | 124230 | 19911.479 | 46.3138 | 2830
| Liquid Hydrogen |  | 30500 | 51621.25 | 120.0703 | 36020 | 60963.85 | 141.801 | 268
| Methyl tertiary butyl ether (MTBE) |  | 93540 | 15093.8487 | 35.1081 | 101130 | 16318.5901 | 37.9568 | 2811
| Ethyl tertiary butyl ether (ETBE) |  | 96720 | 15612.5355 | 36.3145 | 104530 | 16873.2252 | 39.2469 | 2810
| Tertiary amyl methyl ether (TAME) |  | 100480 | 15645.9743 | 36.3923 | 108570 | 16905.687 | 39.3224 | 2913
| Butane |  | 94970 | 19465.6314 | 45.2768 | 103220 | 21156.6018 | 49.2099 | 2213
| Isobutane |  | 90060 | 19287.2122 | 44.8618 | 98560 | 21107.5686 | 49.0959 | 2118
| Isobutylene |  | 95720 | 19271.0319 | 44.8241 | 103010 | 20738.7066 | 48.2379 | 2253
| Propane |  | 84250 | 19903.6237 | 46.2955 | 91420 | 21597.4989 | 50.2355 | 1920
| Solid Fuels |  | Btu/ton [2] | Btu/lb [5] | MJ/kg [4] | Btu/ton [2] | Btu/lb [5] | MJ/kg [4]
| Coal (wet basis) [6] |  | 19546300 | 9773.15 | 22.7322 | 20608570 | 10304.285 | 23.9676
| Bituminous coal (wet basis) [7] |  | 22460600 | 11230.3 | 26.1215 | 23445900 | 11722.95 | 27.2674
| Coking coal (wet basis) |  | 24600497.1446 | 12300.2486 | 28.6102 | 25679670 | 12839.835 | 29.8653
| Farmed trees (dry basis) |  | 16811000 | 8405.5 | 19.5511 | 17703170 | 8851.585 | 20.5887
| Herbaceous biomass (dry basis) |  | 14797554.7639 | 7398.7774 | 17.2094 | 15582870 | 7791.435 | 18.1228
| Corn stover (dry basis) |  | 14075990 | 7037.995 | 16.3703 | 14974460 | 7487.23 | 17.4152
| Forest residue (dry basis) |  | 13243490 | 6621.745 | 15.4021 | 14164160 | 7082.08 | 16.4728
| Sugar cane bagasse |  | 12947318 | 6473.659 | 15.0576 | 14062678 | 7031.339 | 16.3548
| Petroleum coke |  | 25370000 | 12685 | 29.5051 | 26920000 | 13460 | 31.3078
Notes:
[1] The lower heating value (also known as net calorific value) of a fuel is defined as the amount of heat released by combusting a specified quantity (initially at 25°C) and returning the temperature of the combustion products to 150°C, which assumes the latent heat of vaporization of water in the reaction products is not recovered.
The higher heating value (also known as gross calorific value or gross energy) of a fuel is defined as the amount of heat released by a specified quantity (initially at 25°C) once it is combusted and the products have returned to a temperature of 25°C, which takes into account the latent heat of vaporization of water in the combustion products.
[2] Btu = British thermal unit.
[3] The heating values for gaseous fuels in units of Btu/lb are calculated based on the heating values in units of Btu/ft3 and the corresponding fuel density values. The heating values for liquid fuels in units of Btu/lb are calculated based on heating values in units of Btu/gal and the corresponding fuel density values.
[4] The heating values in units of MJ/kg, are converted from the heating values in units of Btu/lb.
[5] For solid fuels, the heating values in units of Btu/lb are converted from the heating values in units of Btu/ton.
[6] Coal characteristics assumed by GREET for electric power production.
[7] Coal characteristics assumed by GREET for hydrogen and Fischer-Tropsch diesel production.
Source:
GREET Transportation Fuel Cycle Analysis Model, GREET 1.8b, developed by Argonne National Laboratory, Argonne, IL, released September 5, 2008. https://greet.es.anl.gov/

## Cl OLD (hidden)
Chlorination
A chlorine residual needs to be established between 0.5 and 2.5 mg/L.
Given the residual requirement it makes sense to seek 4-log reduction via chlorination for viruses and bacteria given the insignificant additional chlorine demand to reach this standard.
Protazoa are considered not to be destroyed via chlorination.
Current Study:
| Flowrate | 0.025 | MGD
| Flowrate | 94.6353 | m3/day
| Volume of Cl tank | 2 | m3
| HRT | 30.4326 | minutes
Determining Chlorine Dosage:
1. Determine initial chlorine demand of Ammonia present in treated wastewater
2. Calculate the allowance needed to account for chlorine decay
3. Requirede Chlorine residual for each organism type
| Free Chlorine Calculations: | [7 empty] | Metcalf and Eddy. 2014. Wastewater Engineering: Treatment and Resource Recovery. Pgs 1314-1419.
| Estimated Dose | 4.16 | mg/L
| 1. Insatantaneous TOC demand |  |  | 0.74092 | mgCl2/L
| 1. NH4+-N concentration |  |  | 0.18854 | mgN/L | At a pH of 7.5 and temperature of 30 °C, about 97.5% of ammonia exists in water as ammonium. I assume that as NH4+ reacts with HOCl that the small amount of NH3 converts to NH4+ so that, in the end, NH4+-N concentration is about equal to the NH3-N concentration. |  | (Canadian Council of Ministers of the Environment, 2010)
| Breakpoint ratio |  |  | 7.6 | mg Cl2/ mg NH4+-N |  | (Metcalf and Eddy Solution 1)
| Cl2 dose to reach breakpoint |  |  | 2.1739 | mgCl2/L |  | (Metcalf and Eddy Solution 2a)
| 2. Chlorine Decay |  |  | 0.25278 | mgCl2/L
| 3. Free chlorine concentration |  |  | 1 | mgCl2/L
| Total Cl2 dosage |  |  | 3.4266 | mg/L |  | (Metcalf and Eddy Solution 2b)
| CT (based on free chlorine) |  |  | 52.7505 | mg-min/L
Instantaneous demand of TOC
| A1 | 0.62
| A2 | 0.522
| A3 | 0.302
| A4 | 0.842
| Cl dose | 7
| soluble inert COD | 30.2
| TOC | 10.3
| sTOC | 10.7
| UV254/sCOD | 0.001
| UV254 | 0.0302
| Clinst | 0.74092 | mgCL2/L
Estimate Chlorine Decay
| Chlorine decay constant | 0.41667 | GPS-X
| time (min) | t10 (hr) | Dose (mg Cl2/L) | Available (mg Cl2/L)
| 1 | 0.011667 | 1.9861 | 1.9765
| 2 | 0.023333 | 1.9861 | 1.967
| 3 | 0.035 | 1.9861 | 1.9576
| 4 | 0.046667 | 1.9861 | 1.9483
| 5 | 0.058333 | 1.9861 | 1.939
| 6 | 0.07 | 1.9861 | 1.9298
| 7 | 0.081667 | 1.9861 | 1.9208
| 8 | 0.093333 | 1.9861 | 1.9118
| 9 | 0.105 | 1.9861 | 1.9029
| 10 | 0.11667 | 1.9861 | 1.8941
| 11 | 0.12833 | 1.9861 | 1.8853
| 12 | 0.14 | 1.9861 | 1.8767
| 13 | 0.15167 | 1.9861 | 1.8681
| 14 | 0.16333 | 1.9861 | 1.8596
| 15 | 0.175 | 1.9861 | 1.8512
| 16 | 0.18667 | 1.9861 | 1.8428
| 17 | 0.19833 | 1.9861 | 1.8345
| 18 | 0.21 | 1.9861 | 1.8263
| 19 | 0.22167 | 1.9861 | 1.8182
| 20 | 0.23333 | 1.9861 | 1.8101
| 21 | 0.245 | 1.9861 | 1.8022
| 22 | 0.25667 | 1.9861 | 1.7942
| 23 | 0.26833 | 1.9861 | 1.7864
| 24 | 0.28 | 1.9861 | 1.7786
| 25 | 0.29167 | 1.9861 | 1.7709
| 26 | 0.30333 | 1.9861 | 1.7633
| 27 | 0.315 | 1.9861 | 1.7557
| 28 | 0.32667 | 1.9861 | 1.7482
| 29 | 0.33833 | 1.9861 | 1.7407
| 30 | 0.35 | 1.9861 | 1.7334 | Should equal the target residual

## UV OLD (hidden)
UV
mW*sec/cm2 = mJ/cm2
UV dose required to meet effluent standard of 2.2 MPN/100ml for microfiltration effluent (Tchobanoglous et al. 2014, pg. 1397)
| 40-50 | mJ/cm2
For reclaimed water systems, the recommended design dosage is 80 mJ/cm2 for microfiltration effluent (Tchobanoglous et al. 2014, pg. 1404)
| Chnnel volume |  | m3
| UV intensity |  | mM/cm2
| Transmittance | 85 | % | estimate for MBR
| Flowrate | 0.025 | MGD
| Flowrate | 1.0953 | liters per second
| UV Chamber Length | 100 | in
| UV Chamber Diameter | 5 | in
| Volume | 0.016088 | m3
*based on 50% of unit volume for40 gpm unit
| Design Dose | 100 | mJ/cm2
| Transmittance (x%) | 0.79 | low value for microfiltration effluent
| Flowrate (Q) | 94.6353 | m3/day
| Ft | 0.95 | unitless | fraction of lamp UV output transmitted through quartz sleeve
| Fp | 0.7 | unitless | output may be reduced by 30% after 7000 hours of use
| Lamp % UV output | 85% |  | UV output of low-pressure high intensity lamps can be modulated between 30 and 100% (Tchobanoglous et al. 2014, pg 1385)
| Intensity | 6.783 | mW/cm2
| Nominal Intensity | 12 | mW/cm2 | 8-15 mW/cm2
| Time | 14.688 | seconds
| Dose | 99.6285 | mJ/cm2