## Cover
Life Cycle Inventory Development: AnMBR, Building Scale, Treating Graywater (0.016 MGD)
Prepared by:
Ben Morelli and Sarah Cashman
Eastern Research Group
110 Hartwell Avenue
Lexington, MA 02421-3136
Last updated: 6/11/2019
*sarah.cashman@erg.com

## TOC
Table of Contents
| Water Quality | Water quality parameters associated with the LCI model.
| LCI | Summary of LCI values developed in this workbook.
| LCC | Summary of life cycle costs used to compile the LCCA.
| Equalization | Calculation of LCI values for the equalization unit process.
| Fine Screen | Calculation of LCI values for the fine screen unit process.
| AnMBR | Calculation of LCI values for the AnMBR unit process.
| Biogas Recovery | Calculation of LCI values for the biogas recovery unit process.
| Dissolved Methane | Calculation of the quantity of dissolved methane in AnMBR permeate.
| DHS | Calculation of LCI values for the downflow hanging sponge unit process.
| Ammonia Adsorption | Calculation of LCI values for the ammonia adsorption unit process.
| UV | Calculation of LCI values for the UV disinfection unit process.
| Chlorine | Calculation of LCI values for the chlorination unit process.
| Sources | Documents sources used in workbook.
Hidden | Conversion Factors | Documents conversion factors used in workbook calculations.

## Water Quality
Influent and Effluent Quality
|  |  | Influent Values1 |  | Target Effluent Quality2
| Water Quality Characteristics |  | Mixed WW | Separated GW | Both
| Characteristic | Unit | Medium Strength (Residential & District) | Low Pollutant Load excluding Laundry | Effluent Quality for Unrestricted Urban Use
| Suspended Solids | mg/L | 220 | 94 | <5
| % Volatile Solids | % | 80 | 47 | -
| cBOD5 | mg/L | 203.2 | 167 | -
| BOD5 | mg/L | 235.712 | 194 | <10
| Soluble BOD5 | mg/L | 143.84 | 116 | -
| Soluble cBOD5 | mg/L | 124 | 100 | -
| COD | mg/L | 508 | 333 | -
| Soluble COD | mg/L | 203.2 | 153 | -
| TKN | mgN/L | 35 | 8.5 | -
| Soluble TKN | mgN/L | 21.1 | 6.9 | -
| Ammonia | mgN/L | 20 | 1.9 | -
| Total Phosphorus | mgP/L | 5.6 | 1.1 | -
| Nitrite | mgN/L | 0 | 0 | -
| Nitrate | mgN/L | 0 | 0.64 | -
| Average Summer | deg C | 23 | 30 | -
| Average Winter | deg C | 23 | 30 | -
| Chlorine Residual | mg/L | n/a | n/a | 0.5-2.5
1 See report for documentation
2 from U.S. EPA 2012, page 4-9, Table 4-4 for 'Unrestricted Urban Reuse-Reclaimed Water Quality'

## LCI
Life Cycle Inventory Data Summary
LCI
| Unit Process | Input/Output | Description | Quantity | Quantity Units | Lifespan | Annual Quantity | Quantity per m3
| Fine Screen | Electricity | Operation Energy | 2357.4796 | kWh | 1 | 2357.4796 | 0.10657
| Fine Screen | Screening Disposal | Screening Disposal | 90.1422 | kg | 1 | 90.1422 | 0.0040748
| Fine Screen | Steel | Screen | 444 | kg | 15 | 29.6 | 0.001338
| Equalization | Concrete | Tank | 11.9169 | m3 | 40 | 0.29792 | 1.3467e-05
| Equalization | Steel | Tank | 711.768 | kg | 40 | 17.7942 | 0.00080437
| Equalization | Electricity | Mixing and Aeration | 2346.2762 | kWh | 1 | 2346.2762 | 0.10606
| Chlorination | Concrete | Contact Basin | 3.0305 | m3 | 40 | 0.075762 | 3.4248e-06
| Chlorination | Steel | Contact Basin Rebar | 75.4379 | kg | 40 | 1.8859 | 8.5252e-05
| Chlorination | Electricity | Chlorine pumping/injection | 1788.264 | kwh | 1 | 1788.264 | 0.080837
| Chlorination | Sodium Hypochlorite | Chlorination | 128.0468 | kg NaOCl | 1 | 128.0468 | 0.0057882
| AnMBR | Concrete | Basin | 44.0402 | m3 | 40 | 1.101 | 4.977e-05
| AnMBR | Steel | Rebar+AD Lid | 2352.1241 | kg | 40 | 58.8031 | 0.0026581
| AnMBR | HDPE | Pipe | 114.5785 | kg | 50 | 2.2916 | 0.00010359
| AnMBR | Polyvinyl Fluoride | Membrane | 349.1146 | kg | 10 | 34.9115 | 0.0015781
| AnMBR | Sodium Hypochlorite | Membrane Cleaning | 42.4282 | kg | 1 | 42.4282 | 0.0019179
| AnMBR | Electricity | MBR Operation, Base | 18074.1349 | kwh | 1 | 18074.1349 | 0.81702 | OpenLCA Model Parameter
| AnMBR | Electricity Sensitivity | MBR Operation, Low | 6845.392 | kwh | 2 | 3422.696 | 0.15472 | scour_freq = | 0.18937
| AnMBR | Methane | Process Emissions | 53.5443 | kg | 1 | 53.5443 | 0.0024204
| AnMBR | Sludge Disposal | to Centralized WWTP | 160.486 | m3 | 1 | 160.486 | 0.0072546
| Biogas Recovery | Natural Gas | Avoided | 990.2975 | m3 | 1 | 990.2975 | 0.044765
| DHS | Electricity | Operation Energy | 768.0103 | kWh | 1 | 768.0103 | 0.034717
| DHS | Methane | Process Emissions | 2.8604 | kg | 1 | 2.8604 | 0.0001293
| DHS | Natural Gas | Avoided | 283.6598 | m3 | 1 | 283.6598 | 0.012823
| DHS | Concrete | Tank | 22.4029 | m3 | 40 | 0.56007 | 2.5318e-05
| DHS | Steel | Rebar | 1055.8357 | kg | 40 | 26.3959 | 0.0011932
| DHS | HDPE | air and water dist. Piping | 25.7377 | kg | 50 | 0.51475 | 2.3269e-05
| Zeolite | Zeolite | Media | 2484.6762 | kg | 1 | 2484.6762 | 0.11232
| Zeolite | NaCl (99+%) | Regeneration fluid | 1219.9637 | kg | 1 | 1219.9637 | 0.055147
| Zeolite | NaOH | Rengeneration pH adjustment | 4424.3893 | kg | 1 | 4424.3893 | 0.2
| Zeolite | Electricity | Operation Energy | 744.0649 | kWh | 1 | 744.0649 | 0.033635
| Zeolite | Disposal, Brine Injection | NaCl Solution | 121.9964 | m3 | 1 | 121.9964 | 0.0055147
| UV | Electricity | UV system | 385.704 | kWh | 1 | 385.704 | 0.017435
| UV | Steel | UV system | 22.6796 | kg | 30 | 0.75599 | 3.4174e-05
| Storage | HDPE | Tank | 797.4163 | kg | 40 | 19.9354 | 0.00090116

## LCC
Life Cycle Costs
AnMBR - Building Scale, Graywater
| LCCA Value | Cost Category | Quantity | Quantity Units | Value | Value Units | Cost | Cost Units | Lifespan | Cost Source | Lifespan Reference
| Equalization | Floating Aerator/Mixer | 2 | units/installation | 16573.2722 | $/unit | 33146.5444 | $/lifespan | 20 | CAPDET | CAPDET, mechanical aerator
| Equalization | Direct Cost | n.a. | n.a. | n.a. | n.a. | 14915.945 | $/lifespan | n.a.
| Equalization | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 24511.8696 | $/lifespan | n.a.
| Equalization | Concrete material | 11.9169 | m3/tank | 258 | $/m3 | 3074.5489 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Installation | 11.9169 | m3/tank | 397.88 | $/m3 | 4741.4787 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Rebar material | 0.78459 | short tons/installation | 983 | $/short ton | 771.251 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Installation | 0.78459 | short tons/installation | 1374 | $/short ton | 1078.0253 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Forms | 409.3085 | ft2/installation | 2 | 0 | 818.617 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Form Installation | 409.3085 | ft2/installation | 2.55 | 0 | 1043.7366 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Equalization | Direct Cost | n.a. | n.a. | n.a. | n.a. | 5187.4458 | $/lifespan | n.a.
| Equalization | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 8524.7026 | $/lifespan | n.a.
| Equalization | Annual, Energy | 2346.2762 | kWh/year | 0.19371 | $/kWh | 454.5089 | $/lifespan
| Fine Screen | Annual, Energy | 2357.4796 | kWh/year | 0.19371 | $/kWh | 456.6792 | $/yr | 1 |  | n.a.
| Fine Screen | Equipment & Installation | 2 | Units per Installation | 12034.4596 | $/unit | 24068.9192 | $/installation | 15 | CAPDET | CAPDET, Process Equipment
| Fine Screen | Direct Cost | n.a. | n.a. | n.a. | n.a. | 10831.0137 | $/lifespan
| Fine Screen | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 17798.9658 | $/lifespan
| AnMBR | Annual, Energy | 18074.1349 | kWh/year | 0.19371 | $/kWh | 3501.231 | $/yr | 1 |  | n.a.
| AnMBR | Membrane System | 504.7216 | m2 | 79.6622 | $/m2 | 40207.2531 | $/lifespan | 10 |  | CAPDET, membrane
| AnMBR | Permeate Pumps | 6 | units/installation | 1296.0222 | $/pump | 7776.1334 | $/lifespan | 25 |  | CAPDET, Pumps
| AnMBR | Pump Installation | n.a. | n.a. | 150% | of equipment cost | 11664.2002 | $/lifespan
| AnMBR | Sludge Pumps | 2 | units | 442.281 | $/unit | 884.5619 | $/lifespan | 25 | CAPDET | CAPDET, Pumps
| AnMBR | Pump Installation | n.a. | n.a. | 150% | of equipment cost | 1326.8429 | $/lifespan | 25 | CAPDET | CAPDET, Pumps
| AnMBR | Biogas Recirculation Blower | 2 | units/installation | 4668.9494 | $/unit | 9337.8987 | $/lifespan | 15 | CAPDET | CAPDET, Process Equipment
| AnMBR | Blower Installation | n.a. | n.a. | 100% | of equipment cost | 9337.8987 | $/lifespan | 15 | CAPDET | CAPDET, Process Equipment
| AnMBR | Major Unit Piping (4"") - for Anaerobic Reactor | 36.3518 | m | 98.5 | $/m | 3580.6535 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| AnMBR | Pipe Installation | 36.3518 | m | 115 | $/m | 4180.4584 | $/lifespan | 50 | RSMeans | Scherer 2003
| AnMBR | Major Unit Piping (2"") - for MBR Tank | 75.7278 | m | 54 | $/m | 4089.3036 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| AnMBR | Pipe Installation | 75.7278 | m | 93.36 | $/m | 7069.9516 | $/lifespan | 50 | RSMeans | Scherer 2003
| AnMBR | Minor Piping | n.a. | n.a. | 25% | of major pipe cost | 4730.0918 | $/lifespan | 50 | CAPDET | Scherer 2003
| AnMBR | Mechanical Mixer | 2 | units/installation | 3252 | $/unit | 6504 | $/lifespan | 15 | https://www.mixerdirect.com/collections/flange-mount-20-1000-gallon-mixers/products/3-4-hp-variable-speed-gear-drive-flange-mount-1 | CAPDET, Process Equipment
| AnMBR | Installation Labor | n.a. | n.a. | 150% | of equipment cost | 9756 | $/lifespan
| AnMBR | Floating Cover | 1 | unit/installation | 35203.6457 | $/unit | 35203.6457 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AnMBR | Floating Cover Installation Labor | 45.9104 | hours | 50 | $/hour | 2295.5224 | $/lifespan
| AnMBR | Ancillary Floating Cover Costs | n.a. | n.a. | 23% | of cover cost | 8096.8385 | $/lifespan
| AnMBR | Gas Safety Equipment | 1 | unit/installation | 28118.8119 | $/unit | 28118.8119 | $/lifespan | 15 | CAPDET | CAPDET, Process Equipment
| AnMBR | Gas Safety Equipment Installation | n.a. | n.a. | 90% | of unit cost | 25306.9307 | $/lifespan | 15 | CAPDET | CAPDET, Process Equipment
| AnMBR | Concrete material | 44.0402 | m3/tank | 258 | $/m3 | 11362.3651 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AnMBR | Installation | 44.0402 | m3/tank | 397.88 | $/m3 | 17522.7047 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AnMBR | Rebar material | 2.0443 | short tons/installation | 983 | $/short ton | 2009.5392 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AnMBR | Installation | 2.0443 | short tons/installation | 1374 | $/short ton | 2808.8574 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AnMBR | Forms | 1199.2659 | ft2/installation | 2 | $/ft2 | 2398.5318 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AnMBR | Form Installation | 1199.2659 | ft2/installation | 2.55 | $/ft2 | 3058.128 | $/lifespan | 40 | RSMeans | CAPDET, structural
| AnMBR | Minor Costs |  |  | 11% | of TBCC | 28448.9836 | $/lifespan
| AnMBR | Direct Cost | n.a. | n.a. | n.a. | n.a. | 106218.1595 | $/lifespan
| AnMBR | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 141585.9359 | $/lifespan
| AnMBR | Sodium Hypochlorite, Membrane cleaning | 282.8549 | kg/year | 2 | $/kg | 565.7099 | $/yr
| Downflow Hanging Sponge | Concrete material | 22.4029 | m3/tank | 258 | $/m3 | 5779.9547 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Downflow Hanging Sponge | Installation | 22.4029 | m3/tank | 397.88 | $/m3 | 8913.6759 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Downflow Hanging Sponge | Rebar material | 1.1639 | short tons/installation | 983 | $/short ton | 1144.074 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Downflow Hanging Sponge | Installation | 1.1639 | short tons/installation | 1374 | $/short ton | 1599.1431 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Downflow Hanging Sponge | Forms | 431.0829 | ft2/installation | 2 | $/ft2 | 862.1658 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Downflow Hanging Sponge | Form Installation | 431.0829 | ft2/installation | 2.55 | $/ft2 | 1099.2614 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Downflow Hanging Sponge | Sponge Media (Polyurethane Foam) | 10.0944 | m3 | 325 | $/m3 | 3280.6902 | $/lifespan | 10 | https://www.alibaba.com/product-detail/polyurethane-foam-filter-polyurethane-foam-filter_60469051703.html?spm=a2700.7724857.4.1.680b4a44SlHRyp&s=p
| Downflow Hanging Sponge | Sponge Installation | n.a. | n.a. | 200% | of material cost | 6561.3804 | $/lifespan
| Downflow Hanging Sponge | Blower | 2 | unit/installation | 388.3606 | $/unit | 776.7211 | $/lifespan | 15 | CAPDET | CAPDET, Process Equipment
| Downflow Hanging Sponge | Blower Installation | n.a. | n.a. | 100% | of equipment cost | 776.7211 | $/lifespan | 15 | CAPDET | CAPDET, Process Equipment
| Downflow Hanging Sponge | 20mm PVC pipe, schedule 40 | 14.3693 | m | 17.4 | $/m | 250.026 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| Downflow Hanging Sponge | 20mm Pipe installation labor | 14.3693 | m | 60.35 | $/m | 867.1877 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| Downflow Hanging Sponge | 32mm PVC pipe, schedule 40 | 12 | m | 49.5 | $/m | 594 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| Downflow Hanging Sponge | 32mm Pipe installation labor | 12 | m | 72.61 | $/m | 871.32 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| Downflow Hanging Sponge | Water Dist. Install | n.a. | n.a. | 32% | of equipment cost | 826.4108 | $/lifespan
| Downflow Hanging Sponge | 20mm PVC pipe, schedule 40 | 14.3693 | m | 17.4 | $/m | 250.026 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| Downflow Hanging Sponge | 20mm Pipe installation labor | 14.3693 | m | 60.35 | $/m | 867.1877 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| Downflow Hanging Sponge | 32mm PVC pipe, schedule 40 | 12 | m | 49.5 | $/m | 594 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| Downflow Hanging Sponge | 32mm Pipe installation labor | 12 | m | 72.61 | $/m | 871.32 | $/lifespan | 50 | RSMeans, includes fittings | Scherer 2003
| Downflow Hanging Sponge | Distribution Nozzles | 18 | units/installation | 10 | $/unit | 180 | $/lifespan
| Downflow Hanging Sponge | Water Dist. Install | n.a. | n.a. | 32% | of equipment cost | 884.0108 | $/lifespan
| Downflow Hanging Sponge | Miscellaneous items | n.a. | n.a. | 20% | of equipment cost | 7569.8554 | $/lifespan |  | CAPDET, trickling filter miscellaneous costs
| Downflow Hanging Sponge | Direct Cost | n.a. | n.a. | n.a. | n.a. | 16805.0789 | $/lifespan
| Downflow Hanging Sponge | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 22400.716 | $/lifespan
| Zeolite System | Adsorption Vessel - Steel | 2 | units/install | 46495.2608 | $ for 2 tanks | 46495.2608 | $/lifespan | 40 | CAPDET
| Zeolite System | Feed System (pumps and piping | 1 | unit/install | 11760.8567 | $/install | 11760.8567 | $/lifespan | 25 |  | CAPDET, Pumps
| Zeolite System | Regeneration System | 1 | unit/install | 16259.9569 | $/install | 16259.9569 | $/lifespan | 15 |  | CAPDET, Process Equipment
| Zeolite System | Zeolite Replacement System | 1 | unit/install | 24386.4332 | $/install | 24386.4332 | $/lifespan | 15 |  | CAPDET, Process Equipment
| Zeolite System | Miscellaneous items | n.a. | n.a. | 42% | of equipment cost | 41539.0532 | $/lifespan
| Zeolite System | Direct Cost | n.a. | n.a. | n.a. | n.a. | 36593.9278 | $/lifespan
| Zeolite System | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 63732.7759 | $/lifespan
| Zeolite System | Zeolite | 2484.6762 | kg/year | 0.27558 | $/kg | 684.7217 | $/yr
| Zeolite System | NaCl | 1219.9637 | kg/year | 0.04 | $/kg | 48.7985 | $/yr
| Zeolite System | NaOH | 4424.3893 | kg/year | 0.3 | $/kg | 1327.3168 | $/yr
| Zeolite System | Annual, Energy | 744.0649 | kWh/year | 0.19371 | $/kWh | 144.1365 | $/yr | 1 |  | n.a.
| Chlorinator | Capital, Pumps and Injector | 1 | equipment | 46300.9901 | $/lifespan | 46300.9901 | $/lifespan | 25 | U.S. EPA 2002 | CAPDET, Pumps
| Chlorinator | Direct Cost | n.a. | n.a. | n.a. | n.a. | 20835.4455 | $/lifespan | n.a.
| Chlorinator | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 34239.5822 | $/lifespan | n.a.
| Chlorinator | Concrete material | 3.0305 | m3/tank | 258 | $/m3 | 781.8669 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Installation | 3.0305 | m3/tank | 397.88 | $/m3 | 1205.7722 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Rebar material | 0.083156 | short tons/installation | 983 | $/short ton | 81.7423 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Installation | 0.083156 | short tons/installation | 1374 | $/short ton | 114.2563 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Forms | 63.8849 | ft2/installation | 2 | $/ft2 | 127.7697 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Form Installation | 63.8849 | ft2/installation | 2.55 | $/ft2 | 162.9064 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Basin Direct Cost | n.a. | n.a. | n.a. | n.a. | 1113.4412 | $/lifespan | 40 | RSMeans | CAPDET, structural
| Chlorinator | Basin Indirect Cost | n.a. | n.a. | n.a. | n.a. | 1829.755 | $/lifespan | n.a.
| Chlorinator | Annual, Energy | 1788.264 | kWh/year | 0.19371 | $/kWh | 346.4136 | $/yr | n.a.
| Chlorinator | Sodium Hypochlorite | 853.6451 | kg/year | 2 | $/kg | 1707.2903 | $/yr
| UV Unit (12 GPM) | Capital, Purchased Equipment | 2 | UV Unit | 1042 | $/unit | 2084 | $/lifespan | 30 | Manufacturer Website | CAPDET UV structural
| UV Unit (12 GPM) | UV Installation | n.a. | n.a. | 100% | of equipment cost | 2084 | $/lifespan
| UV Unit (12 GPM) | Direct Cost | n.a. | n.a. | n.a. | n.a. | 1875.6 | $/lifespan
| UV Unit (12 GPM) | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 3082.236 | $/lifespan
| UV Unit (12 GPM) | Annual, Material | 2 | bulb | 40 | $/unit | 80 | $/lifespan | 1.3699 | Manufacturer Website | CAPDET, lamps
| UV Unit (12 GPM) | Annual, Material | 2 | quartz sleeve | 41 | $/unit | 82 | $/lifespan | 5 | Manufacturer Website | CAPDET, quartz sleeves
| UV Unit (12 GPM) | Annual, Electricity | 385.704 |  | 0.19371 | $/kWh | 74.7167 | $/yr | n.a.
| Treated Effluent Storage | Capital, Purchased Equipment | 2 | tanks | 2000 | $/unit | 4000 | $/lifespan | 40 | CAPDET | CAPDET, structural
| Treated Effluent Storage | Tank Installation | n.a. | n.a. | 100% | of equipment cost | 4000 | $/lifespan
| Treated Effluent Storage | Direct Cost | n.a. | n.a. | n.a. | n.a. | 3600 | $/lifespan | n.a.
| Treated Effluent Storage | Indirect Cost | n.a. | n.a. | n.a. | n.a. | 5916 | $/lifespan | n.a.
[6 empty] | Capital Costs | 1153695.3443
| Cost year | Description | Value | Units | Source |  |  | Direct Cost Elements | Direct Cost Factor
| 2016 | Membrane System Cost | 7.4009 | $/ft2 | Hydromantis 2014 |  |  | Mobilization | 0.05
| 2014 | Standard 550 scfm Swing Arm Diffuser | 16000 | $ | Hydromantis 2014 |  |  | Site Preparation | 0.07
| 2014 | Standard 3000 gpm Pump and Driver Unit | 20500 | $ | Hydromantis 2014 |  |  | Site Electrical | 0.15
[8 empty] | Yard Piping | 0.1
[8 empty] | Instrumentation and Control | 0.08
[8 empty] | Lab and Administration Building | n.a.
[8 empty] | Indirect Cost Elements | Indirect Cost Factor
[8 empty] | Miscellaneous Costs | 0.05
[8 empty] | Legal Costs | 0.02
[8 empty] | Engineering Design Fee | 0.15
[8 empty] | Inspection Costs | 0.02
[8 empty] | Contingency | 0.1
[8 empty] | Technical | 0.02
[8 empty] | Profit | 0.15
Hydromantis 2014

## Equalization
Equalization
|  | Parameter | Value | Units | Note/Source |  | LCI Value
|  | Flowrate | 666.6667 | Gallons per Hour (GPH) | calculated
|  | Volume of Equalization Tank | 5760 |  | CAPDET Method
|  | Dimension (square) | 9.165 | ft | assumed
|  | Volume of Equalization Tank | 5758.7629 | gallons | calculated
|  | Volume of Equalization Tank | 21.804 | m3 | GPS-X input, calculated
|  | HRT | 8.64 | hours | calculated
| Hour | Percent of Daily Flow | Gallons per hour | Cumulative Flow (gal) | FLOW difference | Avg. Flow Accumulation (gal)
| 0 | 1% | 160 | 160 | 506.6667 | 666.6667
| 1 | 1% | 160 | 320 | 506.6667 | 1333.3333
| 2 | 1% | 160 | 480 | 506.6667 | 2000
| 3 | 1% | 160 | 640 | 506.6667 | 2666.6667
| 4 | 1% | 160 | 800 | 506.6667 | 3333.3333
| 5 | 3% | 480 | 1280 | 186.6667 | 4000
| 6 | 11% | 1760 | 3040 | -1093.3333 | 4666.6667
| 7 | 15% | 2400 | 5440 | -1733.3333 | 5333.3333
| 8 | 11% | 1760 | 7200 | -1093.3333 | 6000
| 9 | 11% | 1760 | 8960 | -1093.3333 | 6666.6667
| 10 | 8% | 1280 | 10240 | -613.3333 | 7333.3333
| 11 | 3% | 480 | 10720 | 186.6667 | 8000
| 12 | 3% | 480 | 11200 | 186.6667 | 8666.6667
| 13 | 2% | 320 | 11520 | 346.6667 | 9333.3333
| 14 | 2% | 320 | 11840 | 346.6667 | 10000
| 15 | 2% | 320 | 12160 | 346.6667 | 10666.6667
| 16 | 3% | 480 | 12640 | 186.6667 | 11333.3333
| 17 | 3% | 480 | 13120 | 186.6667 | 12000
| 18 | 4% | 640 | 13760 | 26.6667 | 12666.6667
| 19 | 4% | 640 | 14400 | 26.6667 | 13333.3333
| 20 | 5% | 800 | 15200 | -133.3333 | 14000
| 21 | 3% | 480 | 15680 | 186.6667 | 14666.6667
| 22 | 1% | 160 | 15840 | 506.6667 | 15333.3333
| 23 | 1% | 160 | 16000 | 506.6667 | 16000
16000
Aeration Energy Estimate
|  | O2 = | 0.72042 | lb/hr
|  | STE | 5 | lb O2/hp-hr
|  | O2 Transfer Waste/O2 transfer water | 0.9 | fraction
|  | Oxygen Requirement | 15 | mg/L/hour
|  | O2 saturation | 8.6 | mg/L @ 23*C
|  | OTE | 2.8731
|  | Aeration Horsepower | 0.25074 | HP
|  | Specified Horsepower | 0.35 | HP
|  | Floating Aerator Efficiency | 0.877 | Harris et al. 1982
|  | Aeration Energy | 2346.2762 | kWh
calculations from Harris et al. 1982
Equalization Basin Construction
|  | Average Wetted Volume | 21.7993 | m3
|  | Wall Height | 3.4031 | m
|  | Wall Length | 2.7935 | m
|  | Wall Thickness | 0.22866 | m (9 inches)
|  | Top/Bottom thickness | 0.30488 | m (12 inches)
|  | Slab Length | 3.2508 | m
|  | Slab Width | 3.2508 | m
|  | Wall Count | 4 | count
|  | Slab Count | 1 | count
|  | Wall A Area | 38.026 | m2
|  | Wall A Volume | 8.695 | m3
|  | Bottom Volume | 3.2219 | m3
|  | Total Concrete Volume | 11.9169 | m3
|  | Concrete Density | 2300 | kg/m3
|  | Tank Lifespan | 40 | years
|  | Concrete Mass | 9450.9248 | kg
|  | Rebar spacing | 0.3048 | m (center on center)
|  | Rebar Length | 318.857 | m
|  | rebar weight | 711.768 | kg

## Fine Screen
LCI Data for Fine Screening
LCI Value
| Screenings | 5.3217 | ft3/year
| Screenings | 90.1422 | kg/year
| Unit Mass1 | 444 | kg
1 Two units
| BOD/TSS Removal Rate | 7% |  | Tchobanoglous et al. 2014
Energy Requirement, Screening
| Electricity | 2357.4796 | kwh/yr
calculation from Harris et al. 1982
Screening Generation and Disposal
| Plant Location | Screenings Generation (ft3/Mgal)
| Uniontown, PA | 0.9
| East Hartford, CT | 1.33
| Duluth, MN | 0.56
| Lamberts Point WWCP, VA | 1.2
| Village Creek WWTP, TX | 0.72
| County of Milwaukee, WI | 0.6
| Twin Cities Metro, MN | 1.15
| Chicago, IL | 0.83
| Average | 0.91125
from U.S. EPA 2003
| Ratio between mixed WW/Graywater TSS | 0.42727
Used to scale graywater screenings

## AnMBR
AnMBR, Large Residential Building, treating Graywater
LCI Value
| Flowrate | 0.016 | MGD
| Flowrate | 60.5666 | m3/day
| Flowrate | 11.1111 | gpm
| Flowrate | 22121.9465 | m3/year
GPS-X Model
| Parameter | Value | Units | Note
| SRT | 60 | days | Midpoint of GE Range
| HRT | 0.33333 | days | 8 hr HRT given by Smith et al 2014; confirmed by Nelson Fonseca @ GE
| MLSS Concentration | 12000 | mg/L | Midpoint of GE Range
| Maximum Liquid Volume | 30.2833 | m3 | calculated using HRT, safety factor of 1.5
| Operational Liquid Volume | 20.1889 | m3 | calculated using HRT
| Headspace Volume | 8.6524 | m3 | Assume 30% of operational reactor volume (Giménez et al. 2011)
| Total Volume | 38.9357 | m3/day | calculated
| Diameter | 3.5205 | m | assume cylinder
| Height | 4 | m | assume cylinder
| Sidewater Depth | 3.1111 | m | assume cylinder
| SWD/Diameter | 0.88372 | m | aim for ~0.8, ratio for small AD from (Harris et a. 1982)
| Organic Loading Rate | 0.92907 | range of 1-50 kg COD/m3/day
| COD Load | 18.7569 | kg/day | calculated
| COD Removal | 90% |  | Martinez-Sosa et al. 2011, Feickert et al. 2012
| Methane Yield | 0.26 | m3 CH4/kg COD Destroyed | Martinez-Sosa et al. 2011
| Methane Production | 4.3891 | m3 CH4/day | calculated
| Methane Mass, daily | 2.9319 | kg CH4/day | calculated
| Percent Methane | 70% | by volume | Feickert et al. 2012
| BiogasProduction | 6.2702 | m3/day | calculated
| Biogas Energy | 51197.7192 | MJ/yr | calculated
| Thermal Efficiency | 80% |  | CAPDET (HHV)
| Potential Electricity Production | 11377.2709 | kWh/year | calculated
| Flux | 7.5 | LMH | Chang 2014, Lew et al. 2009
| Membrane Area, Necessary | 336.481 | m2 | calculated
| Membrane Area, Installed | 504.7216 | m2 | calculated
| Biogas Recirculation Rate | 0.225 | Nm3/m2/hr | Smith et al. 2014
| Biogas Recirculation | 75.7082 | m3/hour | calculated
| Biogas Recirculation | 44.5602 | cfm | calculated
| Backflush Flux | 40 | LMH | Yoon 2016
| Backflush Flow | 5953.4912 | gpd | calculated
| Effluent COD | 30.969 | mg/L | calculated
| Effluent BOD | 9.2907 | mg/L | Based on BOD/COD ratio of 0.3 (Tchobanoglous et al. 2014)<25mg/L (Martinez-Sosa et al. 2011)
| Effluent TSS | 2 | mg/L | Christian et al. 2010
| Effluent TOC | 26.5449 | mg/L | calculated based on BOD/TOC ratio of 0.35 (Tchobanoglous et al. 2014)
| Effluent Ammonia | 8.5 | mg/L | influent value (conserved)
Disinfection
|  | [Virus] | [protozoa] | [Bacteria]
| LRT Target | >6 | >4.5 | >3.5
| Technology | Log Reduction | Log Reduction | Log Reduction | Associated Dose | Dose Units | Log Reduction Source
| Membrane bioreactor | 5 | 5 | 5 | n/a | n/a | Sharvelle et al. 2017
| Advanced Oxidation, Ozone | 0 | 0 | 0 | - | - | -
| UV | 0 | 4 | 3 | 30 | mj/cm2 | Sharvelle et al. 2017
| Chlorination | 4 | 0 | 4 | 32 | mg-min/L free chlorine (CT) | Sharvelle et al. 2017
| Total LRV | 9 | 9 | 12
Sodium Hypochlorite
| Parameter | Value | Units | Note/Source
| Sodium Hypolchlorite Use1 | 950 | L/cassette | 950L of 12.5% NaOCl is required for cleaning 1, 48 module membrane cassette (GE Power & Water, 2014)
| Surface area per cassette2 | 1649.9596 | m2/cassette | 370 ft2/module, 48 modules per cassette (GE Power & Water, 2014)
| Sodium Hypolchlorite Use | 0.57577 | L/m2/yr | calculated
| Density of 12.5% wt NaOCl | 1.168 | kg/L
| Annual NaOCl, 15% solution (ecoinvent) | 42.4282 | kg/year | calculated, converts 12.5% solution to 15% solution (for ecoinvent)
Sludge Pumping
| Parameter | Value | Units | Note/Source
| Flow | 5.0855e-06 | m3/sec | continuous
| Head | 13.716 | meters | 45 ft, WAS standard pump head (Tarallo et al. 2015)
| Pump Efficiency | 0.6 | - | standard pump efficiency (Tarallo et al. 2015)
| Gravity | 9.81 | m/s2
| Energy* | 0.0015966 | kW | calculated
| Hours of Operation | 8766 | hours | continuous
| Energy Use | 13.9957 | kWh | calculated
*Assumes s.g. of 1.4 and continuous pumping
Permeate Pump Energy Calculation
| Parameter | Value | Units | Note/Source
| Flow | 0.00096184 | m3/sec
| Head | 12.192 | meters | Feickert et al. 2012
| Pump Efficiency | 0.6 | - | standard pump efficiency (Tarallo et al. 2015)
| Gravity | 9.81 | m/s2
| Energy | 0.19173 | kW | calculated
| Hours of Operation | 8760 | hours | assumed
| Energy Use | 1679.5261 | kWh | calculated
Mechanical Mixing of Anaerobic Tank
| HP Requirement | 0.5 | HP/1000ft3 | Harris et al. 1982
| HP Requirement | 0.53472 | HP | calculated
| Power Consumption | 0.39874 | kW | calculated
| Electric Motor Efficiency | 0.877 |  | Harris et al. 1982
| Operation | 7803 | hours/year | calculated, 90% capacity factor
| Energy Use | 3547.764 | kWh | calculated
|  | Nominal Pore Size | 0.04 | µm
|  | Membrane outer diameter | 0.0019 | m
|  | Membrane inner diameter | 0.0008 | m
|  | Module nominal membrane surface area | 31.6 | m2
|  | Module height | 2.198 | m
|  | Module width | 0.844 | m
|  | Module depth | 0.049 | m
Note: Does not subtract volume of pores
|  | Membrane surface area (m2) | 504.7216
|  | Circumference of fiber (m) | 0.005969
|  | Length of fiber required to equal membrane surface area (m) | 84556.7715
|  | Cross-sectional area of fiber (m2) | 2.3326e-06
|  | Total fiber volume (m3) | 0.19724
|  | Density PVDF (g/cm3) | 1.77
|  | Mass of PVDF in 1 cassette (kg) | 349.1146
Tank Storage
|  | Tank Volume | 5000 | gallon
|  | Tank Quantity | 2 | count
|  | Tank Mass | 398.7082 | kg
|  | Total tank mass | 797.4163 | kg
Tank Depot Website
Sludge Production
| SRT | 60 | days
| Anaerobic Reactor MLSS (XA) | 12000 | mg/L
| Anaerobic Reactor Volume (VA) | 20.1889 | m3
| Membrane Tank Volume (VM) | 6.1743 | m3
| Membrane Tank MLSS (XM) | 12000 | mg/L
| Sludge Flow | 0.43939 | m3/day
Pipe Length
| Pipe Length | 119.2645 | ft
| Number Tanks (NT) | 1 | count
| Sidewater Depth (SWD) | 10.2071 | ft
| Diameter (DIA) | 11.5501 | ft
| Number of Batteries (NB) | 1 | count
| Pipe Weight | 114.5785 | kg
Anaerobic Reactor Tank
| Wall | 16.6717 | m3
| Slab | 2.7435 | m3
| Total | 19.4151 | m3
| Wall Area | 52.5332 | m2
| Slab Area | 9.7339 | m2
| Tank Circumference | 11.0598 | m
| Rebar Spacing | 0.3 | m
| Rebar Length | 359.8218 | m
| Rebar Mass | 556.8934 | kg
Infrastructure calculations from Harris et al. 1982
Membrane Tank
| Number of tanks | 3 | count
| Operational tanks | 2 | count
| Tank length | 0.46619 | m
| Tank width | 2.7432 | m
| Tank height | 3.6576 | m
| Liquid Height | 2.414 | m (2/3 of total height)
| Wall thickness | 0.29108 | m
| Slab thickness | 0.3048 | m (12 inches)
| Total tank volume | 14.0326 | m3
| Operational tank volume, of liquid | 6.1743 | m3
| Wall A Length | 2.5629 | m
| Wall B Length | 2.7432 | m
| Wall A Count | 2 | count
| Wall B Count | 4 | count
| Wall Area | 58.8823 | m2
| Total concrete volume | 24.625 | m3
| Rebar Spacing | 0.3048 | m
| Total Rebar Length | 838.4465 | m
| Rebar Mass | 1297.6572 | kg
Length Basis of Membrane Tank
Based on Z-MOD L L70 Packaged MBR Plant from GE
| Modules | 16 | count
| Membrane area | 549.9865 | m2
| Tank Length | 1.524 | m
| Length/m2 membrane area | 0.002771 | m/m2
| Permeate Pipe Size | 2 | in
| Aeration System Pipe Size | 2 | in
| Pipe Length | 75.7278 | m
*one length of pipe along each tank (3) length and width for each the permeate and biogas recirculation systems. Plus vertical header for each system into tanks (3) and from blower/pump (2). Vertical headers are twic the tank height.
| Blower Energy Consumption |  |  |  | Blower Energy Consumption
| airflow | 0.02553 | kg/sec |  | airflow | 0.02553 | kg/sec
| Universal Gas Constant | 8.314 | J/mole*K |  | Universal Gas Constant | 8.314 | J/mole*K
| Temperature | 296.15 | Kelvin |  | Temperature | 296.15 | Kelvin
| k | 1.304 | (methane) |  | k | 1.304 | (methane)
| n | 0.23313 |  |  | n | 0.23313
| efficiency | 0.7 |  |  | efficiency | 0.7
| inlet pressure | 0.94 | atm (based on Hydromantis 2017) |  | inlet pressure | 0.94 | atm (based on Hydromantis 2017)
| outlet pressure | 1.4713 | atm (based on Hydromantis 2017) |  | outlet pressure | 1.4713 | atm (based on Hydromantis 2017)
| Power, Pw | 1.4639 | kW (calc from Tchobanoglous et al. 2014) |  | Power, Pw | 1.4639 | kW (calc from Tchobanoglous et al. 2014)
| Operation | 8766 | hours per year |  | Operation | 1095.75 | hours per year
| Energy Use | 12832.8491 | kWh/year |  | Energy Use | 1604.1061 | kWh/year
|  | 0.5801 | kWh/m3 |  |  | 0.072512 | kWh/m3
| *Range (for continuous sparging) can be from 0.6-1.6 kWh/m3. (Shin et al. 2014) |  |  |  | *Scour 15 minutes every 2 hours (Feickert et al. 2012)
Note on C112: Author: 1000 kg/m3 = 1g/cm3
Wall A
Wall B

## Biogas Recovery
AnMBR Biogas Recovery
LCI Value
Input Values
| Calculations |  | calc
| Floating Cover Calculation Parameters | Values | Units | Source
| AD Tank Diameter | 3.5205 | m | calculated
| AD Tank Surface Area - Steel (Floating Cover) | 9.7339 | m2 | calculated
| # of AD Tanks | 1 |  | CapdetWorks
| Total AD surface area - Steel | 9.7339 | m2 | calculated
| Steel wall cover thickness | 0.635 | cm | Feickert et al. 2012
| cm per m | 100 |  | conversion factor
| Total Volume of Steel for AD Tank(s) | 0.06181 | m3 | calculated
| Methane Recovery Parameters | Values | Units | Source
| Temperature wastewater enters reactor | 30 | C, Average Residential Mixed Wastewater | Feickert et al. 2012
| COD (influent) | 309.69 | mg/L | calculated
| COD reduction | 90% |  | Feickert et al. 2012, Smith et al. 2014
| Methane production rate | 0.26 | m3 per kg COD | Martinez-Sosa et al. 2011
| Methane gas density | 0.668 | kg/m3 (normal temperature and pressure) | Feickert et al. 2012
| Methane production [gas + permeate] | 4.8408e-05 | kg methane/L wastewater treated | calculated
| Methane production [gas + permeate] | 48.4083 | grams CH4 produced/m3 wastewater treated | calculated
| Fugitive Methane Loss Rate | 5% |  | UNFCCC 2012
| Fugitive emissions of methane | 2.4204 | grams CH4 produced/m3 wastewater treated | calculated
| Fugitive emissions of methane | 2.4204e-06 | kg methane/L wastewater treated | calculated
| Fugitive emissions of methane | 53.5443 | kg/year | calculated
| Gaseous methane production (non-permeate) | 3.3058e-05 | kg methane/L wastewater treated (non-dissolved) | calculated
| Gaseous methane production (non-permeate) | 33.0577 | grams CH4 produced/m3 wastewater treated | calculated
| Continuous flow-through rate (liters/sec) | 0.701 | Liters/sec | calculated
| Continuous flow-through rate (m3/sec) | 0.000701 | m3/s | calculated
| Methane combustion efficiency | 99% |  | IPCC 2006
| Available methane | 0.023174 | grams CH4/second | calculated
| Methane combustion rate | 0.022942 | grams CH4/second | calculated
| Methane combusted, annually | 723.9884 | kg/year | calculated
| Avoided Natural Gas | 769.3943 | kg/year | calculated
| Avoided Natural Gas | 990.2975 | m3/year | calculated
| Higher heating value CH4 | 55.5 | kJ/g | Feickert et al. 2012
| CH4 combustion energy | 1.2733 | kW | calculated
| Boiler efficiency | 80% | CAPDET (HHV) | CAPDET
| Heat from methane | 1.0186 | kW | calculated
| Remaining balance | 0.25465 | kW | calculated
| Fraction of methane production dissolved in permeate | 26.71% |  | calculated

## Dissolved Methane
Dissolved Methane in Permeate Calculation
| Henry's Law as reported in Smith et al 2014 | [6 empty] | Equations for Henry's Law Constant from Tchobanoglous et al., 2014, pg 100
Van't Hoff-Arrhenius Relationship
[8 empty] | Log(10) H = (-A/T)+B |  |  | H (atm) | = | 10^(-A/T+B)
For methane:
| For Methane in Permeate: | [6 empty] | A | = | 675.74 |  | T is temperature in Kelvin
| PCH4 | = | 0.65 | atm | Partial pressure of methane |  |  | B | = | 6.88
| HCH4 @ 30 deg C | = | 44764.9887 | atm | Henry’s constant for methane @ 20 deg C |  |  | Henry’s constant for methane
| M | = | 55.5087 | mol/L | Molarity of solution
| MWCH4 | = | 16.0423 | g/mol | Molecular weight of methane
| OS | = | 1 |  | Oversaturation (assumed not to occur)
|  |  | 1000 | g/kg | Conversion factor
| CH4,dissolved @ 30 deg C | = | 1.293e-05 | kg/L | Dissolved methane concentration @ 20 deg C
For Methane remaining in water after exposure to air:
| HCH4 @ 30 deg C | = | 44764.9887 | atm | Henry’s constant for methane @ 20 deg C
0.016 MGD
| Permeate generated (m3/yr) |  |  |  |  | 22121.9465
Baseline 23 | Dissolved methane in permeate @ 20 deg C (kg/yr) |  |  |  |  | 286.0393 | (input to DHS)
Note on A21: Janet Mosley: Assumes permeate/recycled water is still around the temp of the reactor when permeate/recycled water is exposed to the atmosphere and methane diffuses back into the atmosphere. This is a conservative assumption in terms of total CH4 releases to the air; the higher the temperature, the greater amt of methane that is released from the permeate/recycled water to the atmosphere.
Note on D9: ERG: Assume 65% methane by volume
Note on D13: JMosley: 18.0152 g/mol H2O Approx density of H2O: 1000 g/L
Note on F15: ERG: Brian Crone says the literature shows that oversaturation does not tend to be an issue in well mixed reactors. Given that AnMBR is modeled with sparging, good mixing is assumed. Oversaturation is more likely in reactors with a low velocity profile such as UASB

## DHS
Downflow Hanging Sponge
Permeate methane removal, COD/BOD polishing and partial nitrification. |  |  |  |  | LCI Value
Two DHS reactors are operated in sequence. Both have an HRT of 2 hours.
Unit Sizing
| Parameter | Value | Units | Source
| Reactor HRT | 2 | hours | Matsuura et al. 2015
| Sponge Volume | 5.0472 | m3 | Tembo 2014
| Reactor Volume | 11.4709 | m3 | Matsuura et al. 2015
| Cylinder Height | 2 | meter | Matsuura et al. 2015
| Cylinder Diameter | 2.7023 | meter | calculated
| surface area | 5.7355 | m2 | calculated
Unit Operation
| Parameter | Average Value | Units | Source |  |  | AnMBR effluent |  | Recovery Gas
| Recovered Methane (Stage 1) | 72.5% | of influent dissolved CH4 (from AnMBR) | Matsuura et al. 2015
| Reactor Temperature | 10 to 28 | degrees C | Matsuura et al. 2015
| Removed Methane (Stage 2) | 99% | of influent dissolved CH4 (from Stage 1) | Matsuura et al. 2015
| Sponge Volume fraction | 44% | of reactor volume | Matsuura et al. 2015
| Sponge Void Space | 98% | v/v | Onodera et al. 2016
| Stage 1 airflow (Air1) | 312.5 | L/m3/day | Matsuura et al. 2015
| Stage 2 airflow (Air2) | 2500 | L/m3/day | Matsuura et al. 2015
| Airflow | 1.3443 | m3/hour | calculated
| Airflow | 0.7912 | cfm | calculated | (input to LCCA)
| COD Removal | 55.37% | of influent | calculated from Matsuura et al. 2015
| BOD Removal | 73.47% | of influent | calculated from Matsuura et al. 2016
| Ammonia Removal | 22.22% | of influent | calculated from Matsuura et al. 2017
| Permeate Methane, in Influent | 286.0393 | kg/year | linked
| Recovered Methane (Stage 1) | 207.3785 | kg/year | calculated
| Methane Emissions | 2.8604 | kg/year | calculated
| Influent COD | 30.969 | mg/L | linked
| Influent BOD | 9.2907 | mg/L | linked
| Influent Ammonia | 8.5 | mg/L | linked
| Effluent COD | 13.8209 | mg/L | calculated |  |  | Air1 | Effluent |  | Air2
| Effluent BOD | 2.4649 | mg/L | calculated
| Effluent TOC | 7.0425 | mg/L | calculated based on BOD/TOC ratio of 0.35 (Tchobanoglous et al. 2014)
| Effluent Ammonia | 6.6111 | mg/L | calculated
| Avoided Natural Gas | 220.3845 | kg/year | calculated
| Avoided Natural Gas | 283.6598 | m3/year | calculated
DHS COD Removal from Matsuura et al. 2015
| Season | Summer 2008 | Fall 2008 | Winter 2008 | Spring | All Season
| Influent COD | 110 | 106 | 127 | 150 | 121
| Effluent COD | 47 | 42 | 65 | 65 | 54
| Influent BOD | 43 | 41 | 51 | 61 | 49
| Effluent BOD | 11 | 10 | 17 | 18 | 13
| Influent Ammonia | 27 | 25 | 25 | 29 | 27
| Effluent Ammonia | 18 | 18 | 22 | 30 | 21
| COD Removal | 57.27% | 60.38% | 48.82% | 56.67% | 55.37%
| BOD Removal | 74.42% | 75.61% | 66.67% | 70.49% | 73.47% |  | Off Gas |  | Effluent
| Ammonia Removal | 33.33% | 28% | 12% | -3.448% | 22.22%
Pumping Energy
| Parameter | Value | Units | Note/Source
| Flow | 0.000701 | m3/sec | continuous
| Head | 6 | meters | height of reactor times 1.5, flows down by gravity
| Pump Efficiency | 0.6 | - | standard pump efficiency (Tarallo et al. 2015)
| Gravity | 9.81 | m/s2
| Energy* | 0.068766 | kW | calculated
| Hours of Operation | 8766 | hours | continuous
| Energy Use | 602.805 | kWh | calculated
Blower Energy Consumption
| airflow | 0.00045742 | kg/sec
| Universal Gas Constant | 8.314 | J/mole*K
| Temperature | 293.15 | Kelvin
| k | 1.395 | (air)
| n | 0.28315
| combined blower/motor efficiency | 0.7 | Tarallo et al. 2015
| inlet pressure | 0.98299 | atm
| outlet pressure | 1.3637 | atm
| Pressure drop in inlet filters and piping to blower | 0.017011 | atm (0.25 psi)
| Power, Pw | 0.018859 | kW
| Operation | 8760 | hours per year
| Energy Use | 165.2054 | kWh/year
Polyurethane Sponge
| Sponge Volume | 10.0944 | m3
| Sponge Weight | 5551.9373 | kg (both reactors)
| Unit Cost | 250 | $/m3
| Total Cost | 2523.6079 | $
Tank materials
| Number of tanks | 2 | count
| Diameter | 8.8659 | ft
| SWD | 6.5617 | ft
| wall thickness | 9.5404 | in
| Slab concrete volume | 6.1489 | m3, per tank
| Wall concrete volume | 5.0526 | m3, per tank
| Wall Area | 20.0245 | m2, one tank
| Slab Area | 5.7355 | m2, one tank
| Tank Circumference | 8.4896 | m
| Rebar Spacing | 0.3 | m
| Tank Rebar Length | 226.3905 | m, one tank two layers two vertical and horizontal
| Slab Rebar Length | 114.7094 | m, one tank two layers two vertical and horizontal
| Rebar Mass | 1055.8357 | kg, both tanks
| Pipe Weight | 25.7377 | kg, both tanks
Infrastructure Calculations from Harris et al. 1982
Water Distribution System
Assume 3x3 m square
| Nozzle Distribution Diameter | 1.524 | m
| Pipe length | 2.3949 | m
2 pipes separated by 3 meters
| Distribution piping | 7.1847 | m
| Flowrate approaching manifold | 11.1111 | gpm
| Flowrate in each distribution branch | 5.5556 | gpm
| Main Pipe Size | 1 | in
| Mainfold Pipe Size | 0.75 | in
| Dollar Year | Parameter | Cost | Cost Units | Note | Source
| 2017 | 150mm PVC pipe, schedule 40 | 85.5 | $/m | includes couplings | RSMeans 2016
| 2017 | 150 mm Pipe installation labor | 141.25 | $/m | labor + install equipment | RSMeans 2016
| 2017 | 125mm PVC pipe, schedule 40 | 126 | $/m | includes couplings | RSMeans 2016
| 2017 | 125 mm Pipe installation labor | 128.25 | $/m | labor + install equipment | RSMeans 2016
| 2017 | 100mm PVC pipe, schedule 40 | 98.5 | $/m | includes couplings | RSMeans 2016
| 2017 | 100mm Pipe installation labor | 115 | $/m | labor + install equipment | RSMeans 2016
| 2017 | 50mm PVC pipe, schedule 40 | 54 | $/m | includes couplings | RSMeans 2016
| 2017 | 50mm Pipe installation labor | 93.36 | $/m | labor + install equipment | RSMeans 2016
| 2017 | 40mm PVC pipe, schedule 40 | 50 | $/m | includes couplings | RSMeans 2016
| 2017 | 40mm Pipe installation labor | 84.87 | $/m | labor + install equipment | RSMeans 2016
| 2017 | 32mm PVC pipe, schedule 40 | 49.5 | $/m | includes couplings | RSMeans 2016
| 2017 | 32mm Pipe installation labor | 72.61 | $/m | labor + install equipment | RSMeans 2016
| 2017 | 20mm PVC pipe, schedule 40 | 17.4 | $/m | includes couplings | RSMeans 2016
| 2017 | 20mm Pipe installation labor | 60.35 | $/m | labor + install equipment | RSMeans 2016
Note on C88: Ben Morelli: factor of 2 accounts for roof
Note on C95: Ben Morelli: factor of 6 accounts for 2 rebar layers, 2 directions (vertical and horizontal), and 2 slabs per tank including the roof.

## Ammonia Adsorption
Ammonia Removal - Xeolite Ion Exchange
|  |  | LCI Value |  | Zeolite Regeneration System - Deng et al. 2014
LCI Value
Values Entered
Calculations
| Parameter | Average Performance | Units | Source
| Average Ammonium Removal | 3.0522 | (mg NH4/g zeolite/cycle) | Deng et al. 2014 average
| Average Ammonium Removal | 95% | of influent Ammonium | Deng et al. 2014
| Influent Ammonia Concentration | 6.6111 | mg NH4/L | linked
| Effluent Ammonia Concentration | 0.33056 | mg NH4/L | calculated
| Average Ammonium Load to Zeolite | 146.2506 | kg per year
| Average Ammonium Load to Zeolite | 0.40041 | kg per day
Based on the average breakthrough time a continuous zeolite bed will be in operation for 24 hours before regenerating for 24 hours.
| Required zeolite ammonium capacity | 0.38039 | kg per day
| Minimum required Zeolite | 124.628 | kg
| Extra Zeolite | 604 | kg
| Reactor zeolite | 728.628 | kg zeolite
| Reactor volume | 0.42036 | m3
| Flowrate | 6.0034 | Bed Volume/hour
| Purchased Zeolite | 2484.6762 | kg zeolite per year
| Purchased Zeolite | 6.8027 | kg zeolite per day
| Number of Regenerations | 9 | count | Deng et al. 2014
| Estimated Zeolite Price | 250 | $/short ton | https://www.alibaba.com/product-detail/50-70mesh-Zeolite-Clinoptilolite-Zeolite-Price_60702146861.html?spm=a2700.7724857.main07.57.31882e6a6XWmI4
| Annual Cost | 621.169 | $/year
| Zeolite Density | 1.7333 | kg/L | calculated from Deng et al. 2014
Zeolite Chemical Regeneration
| Parameter | Average Performance | Units | Source
| NaCl Requirement | 3.4543 | g Na+ / g Zeolite NH4 | Deng et al. 2014, adjusted to be on the basis on NH4, not NH4-N
| Annual NaCl Requirement | 1219.9637 | kg /year | calculated
| NaCl Molar Mass | 58.44 | g/mol | periodic table
| Na+ Molar mass | 22.99 | g/mol | periodic table
| NaCl Cost | 40 | $/metric ton | Alibaba: https://www.alibaba.com/product-detail/hot-sale-factory-price-refined-salt_60719657762.html?spm=a2700.7724838.2017115.112.59cd7c45hE3BLH&s=p
| Annual NaCl Cost | 48.7985 | $/yr | calculated
| Concentration | 10 | g/L | Deng et al. 2014
| Water Requirement | 121.9964 | m3/year | for NaCl solution, NaOH added to same water.
| NaOH Dose | 0.2 | kg/m3 wastewater | Deng et al. 2014
| Annual NaOH requirement | 4424.3893 | kg | calculated
| NaOH Cost | 300 | $/ton | Alibaba: https://www.alibaba.com/trade/search?fsb=y&IndexArea=product_en&CatId=&SearchText=NaOH
| Annual NaOH Cost | 1327.3168 | $/yr | calculated
Zeolite adsorption capacity (from Deng et al. 2014)
| Regeneration Cycle | AEC (mg-N/g zeolite) | Breakthrough time | AEC Capacity (% of starting, zone 1)
| Initial | 3.1 | 42 | 100%
| regeneration 1 | 2.7 | 42 | 87.1%
| regeneration 2 | 2.8 | 21 | 90.32%
| regeneration 3 | 2.8 | 21 | 90.32%
| regeneration 4 | 2.4 | 17 | 77.42%
| regeneration 5 | 2.4 | 16 | 77.42%
| regeneration 6 | 2 | 13 | 64.52%
| regeneration 7 | 1.8 | 12 | 58.06%
| regeneration 8 | 1.8 | 13 | 58.06%
| regeneration 9 | 1.9 | 12 | 61.29%
| Average | 2.37 | 20.9
Wastewater Pumping
| Parameter | Value | Units | Note/Source
| Flow | 0.000701 | m3/sec | continuous
| Head | 7.0164 | m | assumed
| Pump Efficiency | 0.6 | - | standard pump efficiency (Tarallo et al. 2015)
| Gravity | 9.81 | m/s2
| Energy* | 0.080416 | kW | calculated
| Hours of Operation | 8766 | hours | continuous
| Energy Use | 704.9247 | kWh | calculated
NaCl Pumping
| Parameter | Value | Units | Note/Source
| Flow | 0.00046707 | m3/sec | 4 BV per hour
| Head | 7.0164 | m | assumed
| Pump Efficiency | 0.6 | - | standard pump efficiency (Tarallo et al. 2015)
| Gravity | 9.81 | m/s2
| Energy* | 0.05358 | kW | calculated
| Hours of Operation | 730.5 | hours | continuous
| Energy Use | 39.1402 | kWh | calculated
Deng Bench Scale System
Used to determine system dimensions.
| Diameter | 6.35 | cm
| Height | 45.7 | cm
| surface area | 31.6692 | cm2
| Total volume | 1.4473 | liters
| Zeolite bed volume | 0.75 | liters
| Zeolite bed height | 23.6823 | cm
| Zeolite bed height/diameter | 3.7295
Reactor Size - This Analysis
Scale up bench system to meet capacity required for 0.025 MGD.
| Zeolite bed volume | 0.42036 | m3
| Diameter | 0.5236 | m
| Surface Area | 0.21532 | m2
| Zeolite bed height | 1.9528 | m
| Flowrate | 2.5236 | m3/hour
| HRT | 0.16657 | hr
| Total Reactor Height | 3.7683 | m
Head loss in a packed column
Used to determine pumping energy
| Delta P | 7.0164 | m of head
| Particle diameter | 0.00048 | m
| Height | 1.9528 | m
| Viscocity | 0.00089 | Pa.s
| Particle Density | 1300 | kg/m3
| Fluid Density | 1000 | kg/m3
| Bed Void Space | 0.3 | ratio of 0.48 mm sand
| Gravitational constant | 9.81 | m/s2
| Velocity | 0.0032556 | m/s
| friction factor | 0.3 | Hassan et al. 2014
calculation from https://neutrium.net/fluid_flow/pressure-drop-through-a-packed-bed/
NaCl Disposal
| Brine Volume | 121.9964 | m3/yr
| Brine | 0.0055147 | m3 brine/m3 wastewater
Nutrient Removal Brine Injection Inventory Data
| Annual Brine Quantity | 2488718.9774 | m3
| Electricity Consumption | 1.8483 | kWh/m3 brine
| Building | 6.7505e-05 | m2/m3 brine
| Pump Steel | 0.00015108 | kg/m3 brine (25 year lifespan)
from Nutrient removal unit process
Values applied to mixed WW process also.
Note on D33: Ben Morelli: corresponds to 4.2 g Na+ / g zeolite NH4-N

## UV
UV Dose Calculations
Sheet Description: The calculations presented on this sheet relate nominal bulb intensity to the delivered UV intensity and dosage. Dosages (in mJ/cm2) relate directly to target log reductions. Delivered UV intensity is determined by wastewater transmittance, bulb sleeve transmittance, lamp UV output, and a lamp aging factor. Dosage is calculated as the product of delivered UV intensity and the duration of UV exposure (in seconds). UV chamber diameter is fixed at 5 inches. Chamber length can be altered to meet a specific UV dose target. Regardless of the necessary LRT a minimum UV dosage of 30 mj/mc2 is applied whenever this technology is utilized (BGLUMR 2013).
User Input Values
LCI Quantity
Unit Note: mW*sec/cm2 = mJ/cm2
| Parameter | Value | Units | Note
| Flowrate | 0.016 | MGD | user specified
| Flowrate | 0.701 | liters per second
| Flowrate | 11.1111 | gpm | Equalization tank allows for treatment of a consistent flowrate
| UV Chamber Length | 32 | in | user specified
| UV Chamber Diameter | 5 | in | based on commercial unit size
| Volume | 0.0051481 | m3 | calculated
*based on 50% of unit volume for40 gpm unit
Calculate delivered UV lamp intensity from nominal intensity*
| Parameter | Value | Units | Note
| Target design dose | 30 | mJ/cm2 | see link
| Transmittance (x%) | 0.79 | low value for microfiltration effluent | Tchobanoglous et al. 2014
| Quartz sleeve transmittance (Ft) | 0.85 | unitless | estimated from Pirnie et al. 2006
| Aging Factor (Fp) | 0.7 | unitless | Hiltunen et al. 2002
| Lamp % UV output | 0.85 | unitless | UV output of low-pressure high intensity lamps can be modulated between 30 and 100% (Tchobanoglous et al. 2014, pg 1385)
| Intensity | 4.046 | mW/cm2 | delivered intensity
| Nominal Intensity | 8 | mW/cm2 | 8-15 mW/cm2
| Time | 7.344 | seconds | duration of UV exposure (reasonable range 2-21 seconds (Qasim 1999))
| Calculated Dose | 29.7138 | mJ/cm2 | should be close to 'Target design dose'
Electricity Consumption
| Parameter | Value | Units | Note/Source
| Power | 0.044 | kW | Atlantic Ultraviolet 2007 for 12 GPM unit
| Hours per year | 8766 | hours
| Electricity Consumption | 385.704 | kWh
Infrastructure
| Unit Mass | 22.6796 | kg | Atlantic Ultraviolet 2007 for 12 GPM unit, mass of 2 units

## Chlorine
Chlorination
Sheet Description: The calculations presented on this sheet estimate target chlorine residuals and conctact times (CT) based on free chlorine dosage (mg/L), instantaneous demand, and chlorine decay. A targeted free chlorine residual of 1 mg/L was selected based on the recommended range of 0.5-2.5 mg/L. Instantaneous demand of both TOC and Ammonia is calculated. Given the residual requirement and a standard contact time of 30 minutes achieving 4-log reduction of bacterial and viral pathogens does not lead to significant increases in chemical dosage. No log reduction of protozoa is assumed to occur.
Current Study:
| Flowrate | 0.016 | MGD |  |  | User Input Values
| Flowrate | 60.5666 | m3/day |  |  | LCI Quantity
| Volume of Cl disinfection tank | 1.25 | m3
| HRT | 29.7194 | minutes (15 is minimum BGLUMR 2014)
Free Chlorine Calculations:
| Estimated Dose (as available Cl) | 5.5126 | mg/L
| Target Residual Achieved based on above dosage | 2.3029 | mg/L free chlorine
| NaOCl Solution Strength | 15% | sodium hypochlorite by wt
| NaOCl , 15%, Solution Strength1 | 14.29% | available chlorine by wt
| Associated NaOCl Dosage (mg/L) | 38.5882 | mg NaOCl, 15% solution/L
| Annual NaOCl Requirement | 128.0468 | kg NaOCl, 15% solution (in ecoinvent)
| Chlorine Requirement | 0.73608 | lb Cl/day
| 1. Insatantaneous TOC demand |  |  | 0.36158 | mgCl2/L
| 1. NH4+-N concentration |  |  | 0.33056 | mgN/L | At a pH of 7.5 and temperature of 30 °C, about 97.5% of ammonia exists in water as ammonium. I assume that as NH4+ reacts with HOCl that the small amount of NH3 converts to NH4+ so that, in the end, NH4+-N concentration is about equal to the NH3-N concentration. | (Canadian Council of Ministers of the Environment, 2010)
| Breakpoint ratio |  |  | 7.6 | mg Cl2/ mg NH4+-N (Tchobanoglous et al. 2014)
| Cl2 dose to reach breakpoint |  |  | 2.8738 | mgCl2/L
| 2. Chlorine Decay |  |  | 0.33585 | mgCl2/L
| 3. Free chlorine concentration |  |  | 1 | mgCl2/L
| Total Cl2 dosage |  |  | 4.2097 | mgCl2/L
| CT (based on free chlorine) |  |  | 73.0401 | mg-min/L
Instantaneous demand of TOC
| A1 | 0.62
| A2 | 0.522
| A3 | 0.302
| A4 | 0.842
| Cl dose | 5.5121 | Total Cl2 Dose (enter manually)
| soluble inert COD | 1.5485 | calculated based on COD and GPSX default ratio of 0.05
| TOC | 26.5449 | calculated based on BOD and BOD/TOC ratio (Tchobanoglous et al. 2014)
| sTOC | 9.1055 | calculated based on TOC and GPSX default ratio of 0.34
| UV254/sCOD | 0.001 | GPS-X default
| UV254 | 0.0015485 | calculated UV absorbance at 254nm
| Clinst | 0.36158 | mgCL2/L
*Calculation method from GPS-X technical reference (Hydromantis 2017)
Estimate Chlorine Decay
*Excludes instantaneous demand
| Chlorine decay constant | 0.41667 | GPS-X
| time (min) | t10 (hr) | Dose (mg Cl2/L) | Available (mg Cl2/L)
| 1 | 0.011667 | 2.6388 | 2.626
| 2 | 0.023333 | 2.6388 | 2.6134
| 3 | 0.035 | 2.6388 | 2.6009
| 4 | 0.046667 | 2.6388 | 2.5885
| 5 | 0.058333 | 2.6388 | 2.5762
| 6 | 0.07 | 2.6388 | 2.564
| 7 | 0.081667 | 2.6388 | 2.552
| 8 | 0.093333 | 2.6388 | 2.54
| 9 | 0.105 | 2.6388 | 2.5282
| 10 | 0.11667 | 2.6388 | 2.5165
| 11 | 0.12833 | 2.6388 | 2.5048
| 12 | 0.14 | 2.6388 | 2.4933
| 13 | 0.15167 | 2.6388 | 2.4819
| 14 | 0.16333 | 2.6388 | 2.4706
| 15 | 0.175 | 2.6388 | 2.4595
| 16 | 0.18667 | 2.6388 | 2.4484
| 17 | 0.19833 | 2.6388 | 2.4374
| 18 | 0.21 | 2.6388 | 2.4265
| 19 | 0.22167 | 2.6388 | 2.4157
| 20 | 0.23333 | 2.6388 | 2.405
| 21 | 0.245 | 2.6388 | 2.3944
| 22 | 0.25667 | 2.6388 | 2.3839
| 23 | 0.26833 | 2.6388 | 2.3734
| 24 | 0.28 | 2.6388 | 2.3631
| 25 | 0.29167 | 2.6388 | 2.3529
| 26 | 0.30333 | 2.6388 | 2.3427
| 27 | 0.315 | 2.6388 | 2.3326
| 28 | 0.32667 | 2.6388 | 2.3227
| 29 | 0.33833 | 2.6388 | 2.3128
| 30 | 0.35 | 2.6388 | 2.3029 | Should equal the target residual
Contact Basin
| Average Wetted Volume | 2.1293 | m3
| Total Volume | 4.697 | m3
| Volume Check | 4.6966 | m3
| Scale Factor | 0.8541 | m
| Short Wall Height | 0.78119 | m
| Short Wall Length | 1.6492 | m
| Long Wall Height | 0.78119 | m
| Long Wall Length | 3.6455 | m
| Wall Thickness | 0.10163 | m (4 inches)
| Top/Bottom thickness | 0.15244 | m (6 inches)
| Top/Bottom Length | 3.6455 | m
| Top/Bottom Width | 1.8524 | m
| Long Wall Count | 2 | count
| Short Wall Count | 3 | count (includes internal partition)
| Top/Bottom Count | 2 | count
| Wall area | 63.8849 | ft2
| Short Wall Volume | 0.39278 | m3
| Long Wall Volume | 0.57883 | m3
| Top/Bottom Volume | 2.0589 | m3
| Total Concrete Volume | 3.0305 | m3
| Concrete Density | 2300 | kg/m3
| Tank Lifespan | 40 | years
| Concrete Mass | 6970.1316 | kg
| Rebar spacing | 0.30488 | m (center on center)
| Rebar Length | 75.6595 | m
| rebar weight | 75.4379 | kg
Chlorinator Energy Consumption
| Current | 1.7 | Amp
| Draw | 120 | Volt
| Power (continuous) | 0.204 | kW
| Electricity Use | 1788.264 | kWh/year
| Electricity Use | 0.051771 | kWh/m3
based on power requirements of Stenner Peristaltic, Chemical Feed Pump (assuming liquid NaOCl solution, i.e. not generated onsite)
for linked calculations see RVFW Workbook

## Sources
Sources | General Information
No | Name | Description | Category | Doi | Text reference | Year
1 | Atlantic Ultraviolet 2007 |  |  |  | Atlantic Ultraviolet. 2007. Sanitron Ultraviolet Water Purifiers. https://www.freshwatersystems.com/specifications/sanitronfamilyinfo.pdf. Accessed 2/6/2018
2 | BGLUMR 2014 |  |  |  | (BGLUMR) Board, G. L.-U. M. R. Recommended Standards for Wastewater Facilities; 2014.
3 | Chang 2014 |  |  |  | Chang, S. Anaerobic Membrane Bioreactors (AnMBR) for Wastewater Treatment. Adv. Chem. Eng. Sci. 2014, 4, 56–61.
4 | Christian et al. 2010 |  |  |  | Christian, S., S. Grant, D. Wilso, P. McCarthy, D. Mills, and M. Kolakowski. 2010. The first two years of full-scale anaerobic membran bioreactor operation treating high strength wastewater at Kens Foods Inc. WEF Conference Proceedings: 4019–4033.
5 | Deng et al. 2014 |  |  |  | Deng, Q.; Dhar, B. R.; Elbeshbishy, E.; Lee, H. S. Ammonium Nitrogen Removal from the Permeates of Anaerobic Membrane Bioreactors: Economic Regeneration of Exhausted Zeolite. Environ. Technol. (United Kingdom) 2014, 35 (16), 2008–2017.
6 | Feickert et al. 2012 |  |  |  | Feickert, C. A., K. Guy, and M. Page. 2012. Energy Balance Calculations for an Anaerobic Membrane Bioreactor. Washington, D.C.
7 | GE Power & Water 2014 |  |  |  | GE Power & Water. Z-MOD L Packaged Plants: MBR Platform Systems Featuring LEAPmbr Technology. General Electric 2014.
8 | Giménez et al. 2011 |  |  |  | Giménez, J. B., R. A., L. Carretero, F. Durán, M. V. Ruano, M. N. Gatti, J. Ribes, J. Ferrer, et al. 2011. Experimental study of the anaerobic urban wastewater treatment in a submerged hollow-fibre membran bioreactor at pilot scale. Bioresource Technology 102: 8799–8806. doi:10.1016/j.biortech.2011.07.014.
9 | Glugokencky 2015 |  |  |  | Glugokencky, E. 2015. Globally averaged marine surface annual mean data on atmospheric methane. U.S. Department of Commerce National Oceanic and Atmospheric Administration Earth System Research Laboratory.
10 | Harris et al. 1982 |  |  |  | Harris, R.W.; Cullinane, M. J.; Sun, P. T. Process Design and Cost Estimating Algorithms for the Computer Assisted Procedure for Design and Evaluation of Wastewater Treatment Systems (CAPDET); U.S. Environmental Protection Agency PB82-190455; U.S. Environmental Protection Agency: Washington, D.C., 1982; p 1700.
11 | Harris et al. 1982 |  |  |  | Harris, R.W.; Cullinane, M. J.; Sun, P. T. Process Design and Cost Estimating Algorithms for the Computer Assisted Procedure for Design and Evaluation of Wastewater Treatment Systems (CAPDET); U.S. Environmental Protection Agency PB82-190455; U.S. Environmental Protection Agency: Washington, D.C., 1982; p 1700.
12 | Hiltunen et al. 2002 |  |  |  | Hiltunen, T., Summers, P. & Robinson, R. B. Small Public Water System Technology Guide Volume II: (2002). Available at: http://www.unh.edu/wttac/WTTAC_Water_Tech_Guide_Vol2/.
13 | Hydromantis 2014 |  |  |  | Hydromantis. CAPDETWorks Version 3.0 Software: Rapid Design and Costing Solution for Wastewater Treatment Plants. (2014).
14 | Hydromantis 2017 |  |  |  | Hydromantis. GPS-X 7.0 Technical Reference; 2017.
15 | Impero and Hammler 2015 |  |  |  | Impero, J. & Hammler, K. MBR Screening Part 2: Selecting an MBR screen. the MBR site (2015). Available at: http://www.thembrsite.com/features/mbr-screening-part-2-selecting-an-mbr-screen/.
16 | Lew et al. 2009 |  |  |  | Lew, B.; Tarre, S.; Beliavski, M.; Dosoretz, C.; Green, M. Anaerobic Membrane Bioreactor (AnMBR) for Domestic Wastewater Treatment. Desalination 2009, 243 (1–3), 251–257.
17 | Martinez-Sosa et al. 2011 |  |  |  | Martinez-Sosa, D., B. Helmreich, T. Netter, S. Paris, F. Bischof, and H. Horn. 2011. Pilot-scale anaerobic submerged membrane bioreactor (AnSMBR) treating municipal wastewater: the fouling phenomenon and long-term operation. Water Science & Technology 64: 1804–1811.
18 | Matsuura et al. 2015 |  |  |  | Matsuura, N., M. Hatamoto, H. Sumino, K. Syutsubo, T. Yamaguchi, and A. Ohashi. 2015. Recovery and biological oxidation of dissolved methane in effluent from UASB treatment of municipal sewage using a two-stage closed downflow hanging sponge system. Journal of Environmental Management 151. Elsevier Ltd: 200–209. doi:10.1016/j.jenvman.2014.12.026.
19 | Onodera et al. 2016 |  |  | -1 | Onodera, T.; Takayama, D.; Ohashi, A.; Yamaguch, T.; Uemura, S.; Harada, H. Evaluation of the Resilience of a Full-Scale down-Flow Hanging Sponge Reactor to Long-Term Outages at a Sewage Treatment Plant in India. J. Environ. Manag. 2016, 181, 832–837.
20 | Pirnie et al. 2006 |  |  |  | Pirnie, M., Linden, K. G. & Malley, J. P. J. Ultraviolet disinfection guidance manual for the final long term 2 enhanced surface water treatment rule. 2, (2006).
21 | Qasim 1999 |  |  |  | Qasim, S. R. Wastewater Treatment Plants: Planning, Design, and Operation, 2nd ed.; CRC Press, 1999.
22 | RSMeans 2016 |  |  |  | RSMeans; Building Construction Cost Data. June 7, 2016.
23 | Sharvelle et al. 2017 |  |  |  | Sharvelle, S.; Ashbolt, N.; Clerico, E.; Hultquist, R.; Leverenz, H.; Olivieri, A. Risk-Based Framework for the Development of Public Health Guidance for Decentralized Non-Potable Water Systems; 2017.
24 | Smith et al. 2014 |  |  |  | Smith, A. L.; Stadler, L. B.; Cao, L.; Love, N. G.; Raskin, L.; Steven, J. Navigating Wastewater Energy Recovery Strategies: A Life Cycle Comparison of Wastewater Energy Recovery Strategies : Anaerobic Membrane Bioreactor and High Rate Activated Sludge with Anaerobic Digestion. Environ. Sci. Technol. 2014, No. 48, 5972–5981.
25 | Tarallo et al. 2015 |  |  |  | Tarallo, S.; Shaw, A.; Kohl, P.; Eschborn, R. A Guide to Net-Zero Energy Solutions for Water Resource Recovery Facilities; WERF ENER1C12; IWA Publishing: London, UK, 2015; p 440.
26 | Tchobanoglous et al. 2014 |  |  |  | Tchobanoglous, G. et al. Wastewater Engineering: Treatment and Resource Recovery. (McGraw-Hill Education, 2014).
27 | Tembo 2014 |  |  | -1 | Tembo, E. L. A. Comparison of Down-Flow Hanging Sponge and Woven Fiber Membrane Systems for Treatment of Polluted Canal Water by, Asian Institute of Technology, 2014.
28 | U.S. EPA 2003 |  |  |  | U.S. EPA. Wastewater Technology Fact Sheet, Screening and Grit Removal. (2003).
29 | Yoon 2016 |  |  |  | Yoon, S.-H. Membrane Bioreactor Processes. (CRC Press, 2016).

## Conversion Factors (hidden)
Conversion Factors, Project Constants, and Looksups used throughout workbook
Conversion Factors
| Category | Parameter | Value | Unit | Source
| Area | sqft/m2 | 10.7639
| Area | ft2/acre | 43560
| Area | ft2/m2 | 10.7639
| Cost | $/kW CHP ICE Capital Cost | 1600 | $/kW | Wiser et al. 2010
| Cost | Maintenance Costs CHP ICE | 0.025 | $/kWh | Wiser et al. 2010
| Density | Air | 1.225 | kg/m3 | Sea Level @ 15*C
| Density | Water Density | 999.97 | kg/m³
| Density | biogas Density | 1.214 | kg/m3
| Density | Methane Density | 0.656 | kg/m3
| Density | Compost Density | 453.5929 | kg/m3
| Density | water density | 8.338 | lb/gal @ 60*F
| Density | Ferric Chloride | 1.37 | s.g. | http://edwardschemicals.com/MSDS/water-treatment/FERRIC%20CHLORIDE%2038%20-%2042.pdf
| Density | water density | 8.329 | lb/g at 70*F | http://www.engineeringtoolbox.com/water-specific-volume-weight-d_661.html
| Density | Steel | 8050 | kg/m3
| Distance | m/mile | 1609.34
| Distance | ft/m | 3.2808
| Distance | km/mile | 1.6093
| Energy | HHV to LHV, generic | 0.9 |  | https://www.csemag.com/single-article/understanding-cogeneration-systems/f4ee71595545969c02674b7b029620a1.html?tx_ttnews%5BsViewPointer%5D=1
| Energy | BTU/Dekatherm (DTH) | 1000000
| Energy | MJ/kWh | 3.6
| Energy | Btu/ft3 | 1027
| Energy | BTU/MJ | 947.817 |  | google conversions
| Energy | 1 MCF = | 1000 | ft3 of natural gas
| Energy | kW/HP | 0.7457
| Energy | Biogas Heat Content: | 600 | BTU/ft3 | PES and UTS 2009, Ong et al. 2017 (HHV)
| Energy | Natural Gas | 40.575 | MJ/m3
| Energy | Methane (HHV) | 55.5 | MJ/kg
| Generic | g/kg, ml/L, etc… | 1000
| Infrastructure | Handrail | 2.7216 | kg/ft
| Volume | gal/3 | 264.1721
| Volume | ft3/m3 | 35.3147
| Volume | gallons/ft3 | 7.4805
| Volume | L/gallon | 3.7854
| Volume | m3/yd3 | 0.76455
| Volume | L/m3 | 1000
| Wastewater Characteristics | BOD/cBOD ratio | 1.16 |  | Source: Brake 2007
| Weight | lb/kg | 2.2046
| Weight | kg per short ton | 907.1847
| Weight | kg/mg | 1e-06
| Time | days per year | 365.25
| Time | hours per year | 8760 |  | google conversions
| TIme | minutes per hour | 60
| Time | seconds per hour | 60
| Time | hours per day | 24
| Food Waste, raw, before processing |  | 650 | kg/m3 | EC 2013
| Density of diesel |  | 0.832 | kg/L | MIT Energy Conversions
| Density of solids, wastewater |  | 1400 | kg/m3
| Density of water |  | 1000 | kg/m3
| Food Waste, air filled pore space |  | 48.1% | v/v | Sundberg et al. 2011
| Average Concrete Density | 2300 | kg/m3
| Rebar | [5 empty] | Steel Grating
|  | Rod Size | Rod Weight |  |  |  | Bar Size Inches: | Weight Per Sq. Ft: | Sect. Prop. Ft. of Width:
| Rod Number | (in) | (lb per linear foot) | kg/ft | kg/m |  | 3/4 x 3/16 | 5.67 | Sx=0.194 / 1x=0.73
| 2 | 0.250 = 1/4" | 0.17 | 0.077111 | 0.25299 |  | 1 x 1/8 | 5.15 | Sx=0.228 / 1x=0.114
| 3 | 0.375 = 3/8" | 0.38 | 0.17237 | 0.5655 |  | 1 x 3/16 | 7.35 | Sx=0.344 / 1x=0.171
| 4 | 0.500 = 1/2" | 0.67 | 0.30391 | 0.99707 |  | 1-1/4 x 1/8 | 6.2 | Sx=0.358 / 1x=0.223
| 5 | 0.625 = 5/8" | 1.04 | 0.47174 | 1.5477 |  | 1-1/4 x 3/16 | 9.03 | Sx=0.536 / 1x=0.335
| 6 | 0.750 = 3/4" | 1.5 | 0.68039 | 2.2322 |  | 1-1/2 x 1/8 | 7.35 | Sx=0.515 / 1x=0.387
| 7 | 0.875 = 7/8" | 2.04 | 0.92533 | 3.0359 |  | 1-1/2 x 3/16 | 10.94 | Sx=0.773 / 1x=0.579
| 8 | 1.000 = 1" | 2.67 | 1.2111 | 3.9734 |  | 1-3/4 x 3/16 | 12.62 | Sx=1.052 / 1x=0.902
| 9 | 1.128 = 1 1/8" | 3.4 | 1.5422 | 5.0598 |  | 2 x 3/16 | 14.3 | Sx=1.375 / 1x=1.375
| 10 | 1.270 = 1 1/4" | 4.3 | 1.9504 | 6.3991 |  | 2-1/4 x 3/16 | 15.87 | Sx=1.740 / 1x=1.958
| 11 | 1.410 = 1 3/8" | 5.31 | 2.4086 | 7.9022 |  | 2-1/2 x 3/16 | 17.55 | Sx=2.148 / 1x=2.685
| 14 | 1.693 = 1 3/4" | 7.65 | 3.47 | 11.3845 |  | http://www.directmetals.com/dm/products/bar-grating/carbon-steel-bar-grating.html
| 18 | 2.257 = 2 1/4" | 13.6 | 6.1689 | 20.2391
Pipe Weights
| material/inner diameter | Wt/ft | Unit | kg/m | Wall thickness | Source
| concrete27 | 322 | lb/ft | 479.1888 |  | http://www.theturnerco.com/products/reinforced-concrete-pipe
| metal18 | 93.54 | lb/ft | 139.2028 | 0.5 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal8 | 27.73 | lb/ft | 41.2668 | 0.312 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal12 | 49.61 | lb/ft | 73.8278 | 0.375 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal4 | 11.36 | lb/ft | 16.9055 | 0.25 | http://www.saginawpipe.com/steel_pipe.htm#pipechart1
| metal10 | 41.59 | lb/ft | 61.8927 | 0.375 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal3 | 8.69 | lb/ft | 12.9321 | 0.25 | http://www.saginawpipe.com/steel_pipe.htm#pipechart1
| concrete24 | 265 | lb/ft | 394.3634 |  | http://www.theturnerco.com/products/reinforced-concrete-pipe
| metal6 | 21.06 | lb/ft | 31.3407 | 0.312 | http://www.saginawpipe.com/steel_pipe.htm#pipechart1
| PVC6 | 3.733 | lb/ft | 5.5553 | 0.28 | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC4 | 2.118 | lb/ft | 3.1519 | 0.237 | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC3 | 1.488 | lb/ft | 2.2144 |  | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC2 | 0.72 | lb/ft | 1.0715 |  | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC1.5 | 0.537 | lb/ft | 0.79914 |  | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC1.25 | 0.45 | lb/ft | 0.66967 |  | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC1 | 0.333 | lb/ft | 0.49556 |  | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC0.75 | 0.226 | lb/ft | 0.33633 |  | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC0.5 | 0.17 | lb/ft | 0.25299 |  | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
GREET Fuel Heating Values
| Fuels |  | Lower Heating Value (LHV) [1] |  |  |  | Higher Heating Value (HHV) [1] |  |  | Density
| Gaseous Fuels @ 32 F and 1 atm |  | Btu/ft3 [2] | Btu/lb [3] | MJ/kg [4] |  | Btu/ft3 [2] | Btu/lb [3] | MJ/kg [4] | grams/ft3
| Natural gas |  | 983 | 20267.2259 | 47.1413 |  | 1089 | 22452.705 | 52.2247 | 22
| Hydrogen |  | 290 | 51682.0289 | 120.2116 |  | 343 | 61127.3652 | 142.1814 | 2.5452
| Still gas (in refineries) |  | 1458 | 20162.6287 | 46.898 |  | 1584 | 21905.078 | 50.9509 | 32.8
| Liquid Fuels |  | Btu/gal [2] | Btu/lb [3] | MJ/kg [4] |  | Btu/gal [2] | Btu/lb [3] | MJ/kg [4] | grams/gal
| Crude oil |  | 129670 | 18351.6428 | 42.6857 |  | 138350 | 19580.0863 | 45.543 | 3205
| Conventional gasoline |  | 116090 | 18679.4122 | 43.448 |  | 124340 | 20006.875 | 46.5357 | 2819
| Reformulated or low-sulfur gasoline |  | 113601.5098 | 18210.6734 | 42.3578 |  | 121848.3804 | 19532.6723 | 45.4327 | 2829.5773
| CA reformulated gasoline |  | 113927.154 | 18271.8133 | 42.5 |  | 122174.4341 | 19594.5248 | 45.5766 | 2828.1932
| U.S. conventional diesel |  | 128450 | 18397.1063 | 42.7914 |  | 137380 | 19676.0954 | 45.7663 | 3167
| Low-sulfur diesel |  | 129487.8476 | 18320.1475 | 42.6124 |  | 138490 | 19593.7864 | 45.5749 | 3206
| Petroleum naphtha |  | 116920 | 19320.1249 | 44.9383 |  | 125080 | 20668.5017 | 48.0746 | 2745
| NG-based FT naphtha |  | 111520 | 19081.2361 | 44.3827 |  | 119740 | 20487.6902 | 47.6541 | 2651
| Residual oil |  | 140352.5222 | 16967.6174 | 39.4664 |  | 150110 | 18147.2268 | 42.2102 | 3752
| Methanol |  | 57250 | 8638.7317 | 20.0936 |  | 65200 | 9838.346 | 22.8838 | 3006
| Ethanol |  | 76330 | 11587.1903 | 26.9516 |  | 84530 | 12831.9822 | 29.847 | 2988
| Butanol |  | 99837 | 14774.8988 | 34.3662 |  | 108458 | 16050.7224 | 37.3337 | 3065
| Acetone |  | 83127 | 12721.1795 | 29.5893 |  | 89511 | 13698.1425 | 31.8617 | 2964
| E-Diesel Additives |  | 116090 | 18679.4122 | 43.448 |  | 124340 | 20006.875 | 46.5357 | 2819
| Liquefied petroleum gas (LPG) |  | 84950 | 20037.6862 | 46.6074 |  | 91410 | 21561.4466 | 50.1516 | 1923
| Liquefied natural gas (LNG) |  | 74720 | 20908.2324 | 48.6322 |  | 84820 | 23734.4255 | 55.2059 | 1621
| Dimethyl ether (DME) |  | 68930 | 12416.9812 | 28.8817 |  | 75610 | 13620.3097 | 31.6806 | 2518
| Dimethoxy methane (DMM) |  | 72200 | 10061.1975 | 23.4022 |  | 79196.8954 | 11036.2273 | 25.6701 | 3255
| Methyl ester (biodiesel, BD) |  | 119550 | 16134.0924 | 37.5277 |  | 127960 | 17269.0796 | 40.1676 | 3361
| Fischer-Tropsch diesel (FTD) |  | 123670 | 18593.1307 | 43.2473 |  | 130030 | 19549.3231 | 45.4714 | 3017
| Renewable Diesel I (SuperCetane) |  | 117059 | 18729.0271 | 43.5634 |  | 125294 | 20046.598 | 46.6281 | 2835
| Renewable Diesel II (UOP-HDO) |  | 122887 | 18907.8407 | 43.9794 |  | 130817 | 20127.9793 | 46.8174 | 2948
| Renewable Gasoline |  | 115983 | 18589.6569 | 43.2393 |  | 124230 | 19911.479 | 46.3138 | 2830
| Liquid Hydrogen |  | 30500 | 51621.25 | 120.0703 |  | 36020 | 60963.85 | 141.801 | 268
| Methyl tertiary butyl ether (MTBE) |  | 93540 | 15093.8487 | 35.1081 |  | 101130 | 16318.5901 | 37.9568 | 2811
| Ethyl tertiary butyl ether (ETBE) |  | 96720 | 15612.5355 | 36.3145 |  | 104530 | 16873.2252 | 39.2469 | 2810
| Tertiary amyl methyl ether (TAME) |  | 100480 | 15645.9743 | 36.3923 |  | 108570 | 16905.687 | 39.3224 | 2913
| Butane |  | 94970 | 19465.6314 | 45.2768 |  | 103220 | 21156.6018 | 49.2099 | 2213
| Isobutane |  | 90060 | 19287.2122 | 44.8618 |  | 98560 | 21107.5686 | 49.0959 | 2118
| Isobutylene |  | 95720 | 19271.0319 | 44.8241 |  | 103010 | 20738.7066 | 48.2379 | 2253
| Propane |  | 84250 | 19903.6237 | 46.2955 |  | 91420 | 21597.4989 | 50.2355 | 1920
| Solid Fuels |  | Btu/ton [2] | Btu/lb [5] | MJ/kg [4] |  | Btu/ton [2] | Btu/lb [5] | MJ/kg [4]
| Coal (wet basis) [6] |  | 19546300 | 9773.15 | 22.7322 |  | 20608570 | 10304.285 | 23.9676
| Bituminous coal (wet basis) [7] |  | 22460600 | 11230.3 | 26.1215 |  | 23445900 | 11722.95 | 27.2674
| Coking coal (wet basis) |  | 24600497.1446 | 12300.2486 | 28.6102 |  | 25679670 | 12839.835 | 29.8653
| Farmed trees (dry basis) |  | 16811000 | 8405.5 | 19.5511 |  | 17703170 | 8851.585 | 20.5887
| Herbaceous biomass (dry basis) |  | 14797554.7639 | 7398.7774 | 17.2094 |  | 15582870 | 7791.435 | 18.1228
| Corn stover (dry basis) |  | 14075990 | 7037.995 | 16.3703 |  | 14974460 | 7487.23 | 17.4152
| Forest residue (dry basis) |  | 13243490 | 6621.745 | 15.4021 |  | 14164160 | 7082.08 | 16.4728
| Sugar cane bagasse |  | 12947318 | 6473.659 | 15.0576 |  | 14062678 | 7031.339 | 16.3548
| Petroleum coke |  | 25370000 | 12685 | 29.5051 |  | 26920000 | 13460 | 31.3078
Notes:
[1] The lower heating value (also known as net calorific value) of a fuel is defined as the amount of heat released by combusting a specified quantity (initially at 25°C) and returning the temperature of the combustion products to 150°C, which assumes the latent heat of vaporization of water in the reaction products is not recovered.
The higher heating value (also known as gross calorific value or gross energy) of a fuel is defined as the amount of heat released by a specified quantity (initially at 25°C) once it is combusted and the products have returned to a temperature of 25°C, which takes into account the latent heat of vaporization of water in the combustion products.
[2] Btu = British thermal unit.
[3] The heating values for gaseous fuels in units of Btu/lb are calculated based on the heating values in units of Btu/ft3 and the corresponding fuel density values. The heating values for liquid fuels in units of Btu/lb are calculated based on heating values in units of Btu/gal and the corresponding fuel density values.
[4] The heating values in units of MJ/kg, are converted from the heating values in units of Btu/lb.
[5] For solid fuels, the heating values in units of Btu/lb are converted from the heating values in units of Btu/ton.
[6] Coal characteristics assumed by GREET for electric power production.
[7] Coal characteristics assumed by GREET for hydrogen and Fischer-Tropsch diesel production.
Source:
GREET Transportation Fuel Cycle Analysis Model, GREET 1.8b, developed by Argonne National Laboratory, Argonne, IL, released September 5, 2008. https://greet.es.anl.gov/
| Year | CPI | Year | CPI
| 1970 | 38.8 | 1994 | 148.2
| 1971 | 40.5 | 1995 | 152.4
| 1972 | 41.8 | 1996 | 156.9
| 1973 | 44.4 | 1997 | 160.5
| 1974 | 49.3 | 1998 | 163
| 1975 | 53.8 | 1999 | 166.6
| 1976 | 56.9 | 2000 | 172.2
| 1977 | 60.6 | 2001 | 177.1
| 1978 | 65.2 | 2002 | 179.9
| 1979 | 72.6 | 2003 | 184
| 1980 | 82.4 | 2004 | 188.9
| 1981 | 90.9 | 2005 | 195.3
| 1982 | 96.5 | 2006 | 201.6
| 1983 | 99.6 | 2007 | 207.3
| 1984 | 103.9 | 2008 | 215.3
| 1985 | 107.6 | 2009 | 214.5
| 1986 | 109.6 | 2010 | 218.1
| 1987 | 113.6 | 2011 | 224.9
| 1988 | 118.3 | 2012 | 229.6
| 1989 | 124 | 2013 | 233
| 1990 | 130.7 | 2014 | 236.7
| 1991 | 136.2 | 2015 | 237
| 1992 | 140.3 | 2016 | 240
| 1993 | 144.5 | 2017 | n.a.
Source: BLS Detailed Report 2017
Note on D8: Author: rane of 465 to 1600 for lean burn or 465 to 1200 for advanced generation