## Cover
Building and District Scale Wastewater Treatment for Reuse Applications: Life Cycle Cost Assessment
Prepared by:
Ben Morelli and Sarah Cashman
Eastern Research Group
110 Hartwell Avenue
Lexington, MA 02421-3136
Last Updated: 6/11/2019
*sarah.cashman@erg.com

## TOC
Table of Contents
| LCCA | Compiles all costs for each treatment system and calculates system Net Present Value (NPV).
| Equipment | Documentation of equipment related cost calculations.
| Labor | Documentation of labor related cost calculations.
| ResultsFigures | Report baseline LCCA figures (these are static values generated from LCCA Calculator)
| Sensitivity Analyses | Report sensitivity analyses LCCA figures (these are static values generated from LCCA Calculator)
| Sources | Documents sources used in workbook.
Hidden | Conversion Factors | Documents conversion factors used in workbook calculations.
Hidden | Supporting Info | Documentation of cost factors and tables documenting worksheet development and cost coverage.
Hidden | Lookups | Contains lookup values used for data validation.
Delete or Expand | Checks | Documents additional cost data found to support our numbers. Could be expanded or deleted in final version.

## LCCA
Decentralized Life Cycle Cost Assessment Database and Calculations
This sheet is a calculator that can be used to calculate NPV of the upgraded WWTP over 30 years.
Key:
|  | Calculator Input Value1 |  | Key: | Calculator Output Value
1 Changing these value will affect the output of the worksheet.
LCCA Cost Factors
|  | Description | Quantity | Value | Unit | Source
|  | Assumed LCCA Time Period | years | 30 | years
|  | Electricity | 1 kWh | 0.19371 | $/kWh | Annual Average Small Commercial Electricity Rate in SF (SFWPS 2017)
|  | Assumed discount rate | time value of money | 0.05 | % (as decimel)
|  | Interest | during construction period | 0.017 | % (as decimel) | Low Cost Scenario = 1.7%
|  | Oxygen Cost | kg | 0.1294 | $/kg | $110/ton (in 2011 $s) (Carollo Engineers 2012)
|  | Sodium Hypochlorite (NaOCl) | kg | 0.30495 | $/kg (as 15% solution) | 9.76 $/ft3 (Hydromantis 2014)
|  | Polymer | lb | 1.3 | $/lb | CAPDET
|  | Labor Rate | fully loaded | 50 | $/hour | US DOL 2017, see report for calculations.
|  | Laboratory Labor Rate | fully loaded | 55 | $/hour | 110% of labor rate (Harris et al. 1982)
|  | Annual Maintenance Costs1 | Structural Units & AnMBR | 1.5% | of bare construction cost | storage tanks (City of Alexandria 2015), material and labor cost
|  | Annual Maintenance Costs1 | Electrical/Mechanical Units | 5% | of bare construction cost | material and labor, original factor is 2.5% (CAPDET). for materials only.
|  | Annual Maintenance Costs1 | Fine Screen and pumps | 5% | of bare construction cost | material and labor, original factor is 2.5% (CAPDET). for materials only.
|  | Annual Maintenance Costs | DHS reactor | 1% | of bare construction cost | CAPDET Trickling filter as proxy, materials only
|  | Annual Maintenance Costs | Building GW | 10.47% | of bare construction cost | Harris et al. 1982 (varies with system size)
|  | Annual Maintenance Costs | Building WW | 9.322% | of bare construction cost | Harris et al. 1982 (varies with system size)
|  | Annual Maintenance Costs | District GW | 8.815% | of bare construction cost | Harris et al. 1982 (varies with system size)
|  | Annual Maintenance Costs | District WW | 7.784% | of bare construction cost | Harris et al. 1982 (varies with system size)
|  | Annual Maintenance Costs1 | Disinfection | 3% | of bare construction cost | storage tanks (City of Alexandria 2015), material and labor cost
1 Includes material and labor costs of maintenance.
LCCA Summary Table and Chart
| Capital + Material Replacement | Process Category | Process | Interest During Construction | Capital | O&M Labor | Materials (excluding chemicals and energy) | Chemicals | Energy
| 95823.5431 | Preliminary/Primary | Thermal Recovery | 2443.5003 | 95823.5431 | 17660.3661 | 39764.6825 | 0 | 0
| 110678.7746 | Preliminary/Primary | Equalization | 2822.3088 | 110678.7746 | 48373.3141 | 34013.8311 | 0 | 11251.8561
| 0 | Preliminary/Primary | Clarification | 0 | 0 | 0 | 0 | 0 | 0
| 69600.103 | Preliminary/Primary | Fine Screen | 1774.8026 | 69600.103 | 141789.429 | 28882.5049 | 0 | 9731.2443
| 0 | Biological Treatment | Wetland | 0 | 0 | 0 | 0 | 0 | 0
| 408015.2015 | Biological Treatment | AeMBR | 10404.3876 | 408015.2015 | 400566.0949 | 265306.6178 | 817.0799 | 72170.3183
| 0 | Biological Treatment | AnMBR | 0 | 0 | 0 | 0 | 0 | 0
| 0 | Sludge Handling and Disposal | Dewatering | 0 | 0 | 0 | 0 | 0 | 0
| 0 | Sludge Handling and Disposal | Composting | 0 | 0 | 0 | 0 | 0 | 0
| 0 | Post-Treatment | Zeolite | 0 | 0 | 0 | 0 | 0 | 0
| 0 | Post-Treatment | DHS | 0 | 0 | 0 | 0 | 0 | 0
| 0 | Disinfection | Ozone | 0 | 0 | 0 | 0 | 0 | 0
| 11088 | Disinfection | UV | 282.744 | 11088 | 19982.3263 | 2757.236 | 0 | 1587.747
| 108731.9901 | Disinfection | Chlorination | 2772.6657 | 108731.9901 | 65198.2947 | 40721.9505 | 4085.3994 | 6001.8851
| 547805.7248 | Building Reuse | Building Reuse | 13969.046 | 547805.7248 | 52227.0798 | 62089.079 | 0 | 0
|  | Avoided Utility Costs | Avoided Utility Costs | 0 | 0 | 0 | -2357982.1126 | 0 | 0
| 0 | Other | Administration | 0 | 0 | 1370313.5636 | 0 | 0 | 0
| 1255919.7941 | Total | Total | 34469.4551 | 1351743.3372 | 2116110.4684 | 473535.9017 | 4902.4793 | 100743.0508
| Capital |  | Column Lookup |  | Capital | Labor | Materials | Chemical | Energy
|  | Total NPV including thermal recovery | 4081504.6924 | $
|  | Total NPV less avoided utility costs | 1723522.5798 | $
|  | Total NPV without thermal recovery | 3925812.6005 | $
Unsewered scenario is only available at the district scale
Select Scenario Here:
|  |  | Treatment System | Wastewater Type | System Scale | Reuse Scenario | Sewered/Unsewered | [9 empty] | Residential energy escalation factors (excluding general inflation) California region (Lavappa et al. 2017).
|  | Scenario Select | AeMBR | Mixed WW | Building | Low Reuse | Sewered | [9 empty] | Electricity | 1 | 1 | 0.98 | 0.98 | 0.98 | 1 | 1.02 | 1.06 | 1.07 | 1.07 | 1.09 | 1.1 | 1.1 | 1.1 | 1.11 | 1.11 | 1.12 | 1.13 | 1.13 | 1.14 | 1.15 | 1.15 | 1.16 | 1.16 | 1.17 | 1.18 | 1.19 | 1.2 | 1.21 | 1.22
[17 empty] | Year | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | NPV Values
[18 empty] | 2016: Year # | NPV | Year #
|  | Reuse Scenario | Sewer Scenario | System Size | Treatment System | Wastewater Type | General Cost Category | Detailed Cost Category | Process | Desciption | Cost Inputs | Cost Units | Cost Timing | Expected Life | Source | Note | Present Value (2016) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Ozone | Generator + Ancillary Equipment | 72029 | $ | Year 1 | 10 | Eagleton 1999 | Equipment + Installation | 72029 | 72029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Chemical | Chemicals | Ozone | Oxygen | 603.5 | $/yr | Annual |  |  |  | 9741.138 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 603.5 | 574.7619 | 547.3923 | 521.326 | 496.5009 | 472.858 | 450.341 | 428.8962 | 408.4726 | 389.0215 | 370.4967 | 352.854 | 336.0514 | 320.0489 | 304.8085 | 290.2938 | 276.4703 | 263.3051 | 250.7667 | 238.8254 | 227.4528 | 216.6217 | 206.3064 | 196.4823 | 187.126 | 178.2152 | 169.7288 | 161.6465 | 153.949 | 146.6181
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Ozone | Contact Basin | 1043 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 1043 | 1043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Energy | Electricity | Ozone | Electricity | 1403.4652 | $/yr | Annual |  |  |  | 24319.7189 | 1403.4652 | 1403.4652 | 1375.3959 | 1375.3959 | 1375.3959 | 1403.4652 | 1431.5345 | 1487.6731 | 1501.7077 | 1501.7077 | 1529.777 | 1543.8117 | 1543.8117 | 1543.8117 | 1557.8463 | 1557.8463 | 1571.881 | 1585.9156 | 1585.9156 | 1599.9503 | 1613.985 | 1613.985 | 1628.0196 | 1628.0196 | 1642.0543 | 1656.0889 | 1670.1236 | 1684.1582 | 1698.1929 | 1712.2275 | 1403.4652 | 1336.6335 | 1247.5246 | 1188.1187 | 1131.5416 | 1099.6517 | 1068.2331 | 1057.2615 | 1016.4149 | 968.0142 | 939.1504 | 902.6347 | 859.6521 | 818.7163 | 786.8183 | 749.3507 | 720.0968 | 691.9297 | 658.9807 | 633.1547 | 608.294 | 579.3276 | 556.5383 | 530.0365 | 509.1483 | 489.0476 | 469.7068 | 451.0989 | 433.1982 | 415.9794
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | General | Ozone | General Maintenance | 1088.2575 | $/yr | Annual |  |  |  | 17565.6444 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1036.4357 | 987.0816 | 940.0777 | 895.3121 | 852.6782 | 812.0745 | 773.4043 | 736.5755 | 701.5005 | 668.0957 | 636.2816 | 605.9825 | 577.1262 | 549.644 | 523.4705 | 498.5433 | 474.8031 | 452.1935 | 430.6604 | 410.1528 | 390.6217 | 372.0207 | 354.3054 | 337.4337 | 321.3655 | 306.0623 | 291.4879 | 277.6076 | 264.3882
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Operations Labor | Ozone | Operation Labor | 27500 | $/yr | Annual |  | Hansen et al. 1979 |  | 443879.5234 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 27500 | 26190.4762 | 24943.3107 | 23755.534 | 22624.3181 | 21546.9696 | 20520.9234 | 19543.7366 | 18613.0825 | 17726.7452 | 16882.6145 | 16078.6804 | 15313.029 | 14583.8371 | 13889.3687 | 13227.9702 | 12598.0669 | 11998.1589 | 11426.818 | 10882.6838 | 10364.4608 | 9870.915 | 9400.8715 | 8953.2109 | 8526.8675 | 8120.8262 | 7734.1202 | 7365.8288 | 7015.075 | 6681.0238
|  | Both | Sewered | Building | RVFW | Mixed WW | Energy | Electricity | Wetland | Electricity | 2716.3796 | $/yr | Annual |  |  |  | 47070.3439 | 2716.3796 | 2716.3796 | 2662.052 | 2662.052 | 2662.052 | 2716.3796 | 2770.7072 | 2879.3624 | 2906.5262 | 2906.5262 | 2960.8538 | 2988.0176 | 2988.0176 | 2988.0176 | 3015.1814 | 3015.1814 | 3042.3452 | 3069.509 | 3069.509 | 3096.6728 | 3123.8365 | 3123.8365 | 3151.0003 | 3151.0003 | 3178.1641 | 3205.3279 | 3232.4917 | 3259.6555 | 3286.8193 | 3313.9831 | 2716.3796 | 2587.0282 | 2414.5596 | 2299.5806 | 2190.0768 | 2128.3545 | 2067.5444 | 2046.3091 | 1967.2513 | 1873.5727 | 1817.7074 | 1747.032 | 1663.84 | 1584.6095 | 1522.8715 | 1450.3538 | 1393.7334 | 1339.2166 | 1275.4444 | 1225.4586 | 1177.3411 | 1121.2773 | 1077.1691 | 1025.8753 | 985.4467 | 946.5422 | 909.1084 | 873.0933 | 838.4467 | 805.12
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | HPDE Pipe | 63140 | $ | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 63140 | 63140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | Bed Concrete and Construction | 116698 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 116698 | 116698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | Gravel | 3536 | $ | Year 1 | 10 |  | Equipment + Installation | 3536 | 3536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | Wood Chips | 857 | $ | Year 1 | 2 | RSMeans | Equipment + Installation | 857 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | Pumps | 127277 | $ | Year 1 | 25 | RSMeans for cost, Lifespan CAPDET | Equipment + Installation | 127277 | 127277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | Steel Grating | 61419 | $ | Replace at Lifespan | 40 | RSMeans for cost, Lifespan CAPDET | Equipment + Installation | 61419 | 61419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Maintenance Labor | Wetland | Wetland Maintenance Labor | 20839.3632 | $/yr | Annual |  | Gross et al. 2007a | For the wetland itself (i.e. not pumps) | 336369.6954 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 20839.3632 | 19847.0126 | 18901.9168 | 18001.8255 | 17144.5957 | 16328.1864 | 15550.6537 | 14810.1464 | 14104.9013 | 13433.2394 | 12793.5613 | 12184.3441 | 11604.1372 | 11051.5593 | 10525.2945 | 10024.09 | 9546.7524 | 9092.1452 | 8659.1859 | 8246.8437 | 7854.1368 | 7480.1303 | 7123.9336 | 6784.6987 | 6461.6178 | 6153.9217 | 5860.8778 | 5581.7884 | 5315.989 | 5062.8466
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | Crushed Limestone | 1375 | $ | Year 1 | 10 |  | Equipment + Installation | 1375 | 1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | Direct + Indirect | 445233 | $ | Year 1 |  |  | Direct and Indirect Cost | 445233 | 445233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 445233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | RVFW Effluent Storage | 12000 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 12000 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | General | Wetland | Storage tank Maintanence | 90 | $/yr | Annual |  |  |  | 1452.6966 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 85.7143 | 81.6327 | 77.7454 | 74.0432 | 70.5174 | 67.1594 | 63.9613 | 60.9155 | 58.0148 | 55.2522 | 52.6211 | 50.1154 | 47.7289 | 45.4561 | 43.2915 | 41.23 | 39.2667 | 37.3969 | 35.6161 | 33.9201 | 32.3048 | 30.7665 | 29.3014 | 27.9061 | 26.5772 | 25.3117 | 24.1063 | 22.9584 | 21.8652
|  | Both | Sewered | Building | RVFW | Both | Materials | General | UV | General Maintenance | 77.88 | $/yr | Annual |  |  |  | 1257.0668 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 74.1714 | 70.6395 | 67.2757 | 64.0721 | 61.021 | 58.1153 | 55.3479 | 52.7122 | 50.2021 | 47.8116 | 45.5348 | 43.3665 | 41.3014 | 39.3347 | 37.4616 | 35.6777 | 33.9788 | 32.3607 | 30.8198 | 29.3522 | 27.9544 | 26.6233 | 25.3555 | 24.1481 | 22.9982 | 21.903 | 20.86 | 19.8667 | 18.9207
|  | Both | Sewered | Building | RVFW | Both | Capital | Capital | UV | UV System | 10384 | $/replacement | Replace at Lifespan | 30 | lifespan, CAPDET UV Structural | Equipment + Installation | 10384 | 10384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Both | Energy | Electricity | UV | Operational Electricity | 237.6883 | $/yr | Annual | n.a. |  |  | 4118.7433 | 237.6883 | 237.6883 | 232.9345 | 232.9345 | 232.9345 | 237.6883 | 242.4421 | 251.9496 | 254.3265 | 254.3265 | 259.0803 | 261.4571 | 261.4571 | 261.4571 | 263.834 | 263.834 | 266.2109 | 268.5878 | 268.5878 | 270.9647 | 273.3416 | 273.3416 | 275.7184 | 275.7184 | 278.0953 | 280.4722 | 282.8491 | 285.226 | 287.6028 | 289.9797 | 237.6883 | 226.3698 | 211.2785 | 201.2176 | 191.6358 | 186.235 | 180.914 | 179.0559 | 172.1382 | 163.9411 | 159.0528 | 152.8686 | 145.5891 | 138.6563 | 133.2541 | 126.9087 | 121.9543 | 117.184 | 111.6038 | 107.2299 | 103.0196 | 98.1139 | 94.2543 | 89.766 | 86.2284 | 82.8242 | 79.5487 | 76.3973 | 73.3657 | 70.4495
|  | Both | Sewered | Building | RVFW | Both | Materials | Materials | UV | Bulbs | 350.365 | $/replacement | Replace at Lifespan | 1 | lifespan 12000 hours (U.S. EPA 2002), | Equipment + Installation | 5219.7818 | 0 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 350.365 | 0 | 0 | 333.6809 | 317.7914 | 302.6584 | 288.2461 | 274.5201 | 261.4477 | 248.9978 | 237.1408 | 225.8484 | 215.0937 | 204.8511 | 195.0963 | 185.806 | 176.9581 | 168.5315 | 160.5062 | 152.8631 | 145.5839 | 138.6513 | 132.0489 | 125.7608 | 119.7722 | 114.0688 | 108.6369 | 103.4637 | 98.5369 | 93.8447 | 89.3759 | 0
|  | Both | Sewered | Building | RVFW | Both | Materials | Materials | UV | Quartz Sleeve | 228 | $/replacement | Replace at Lifespan | 5 | lifespan, CAPDET Quartz Sleeve | Equipment + Installation | 610.6253 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.5762 | 0 | 0 | 0 | 0 | 146.9708 | 0 | 0 | 0 | 0 | 115.1555 | 0 | 0 | 0 | 0 | 90.2273 | 0 | 0 | 0 | 0 | 70.6955 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | All | All | Both | Labor | Operations Labor | UV | Operation Labor | 1200 | $/yr | Annual |  | Hansen et al. 1979 |  | 19369.2883 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1142.8571 | 1088.4354 | 1036.6051 | 987.243 | 940.2314 | 895.4585 | 852.8176 | 812.2072 | 773.5307 | 736.6959 | 701.6151 | 668.2049 | 636.3856 | 606.0815 | 577.2205 | 549.7338 | 523.556 | 498.6248 | 474.8807 | 452.2674 | 430.7308 | 410.2198 | 390.6856 | 372.0815 | 354.3633 | 337.4889 | 321.418 | 306.1124 | 291.5356
|  | Both | Sewered | Building | All | Mixed WW | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage | 12000 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 12000 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All | Mixed WW | Materials | General | Building Reuse | Storage tank Maintanence | 90 | $/yr | Annual |  |  |  | 1452.6966 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 85.7143 | 81.6327 | 77.7454 | 74.0432 | 70.5174 | 67.1594 | 63.9613 | 60.9155 | 58.0148 | 55.2522 | 52.6211 | 50.1154 | 47.7289 | 45.4561 | 43.2915 | 41.23 | 39.2667 | 37.3969 | 35.6161 | 33.9201 | 32.3048 | 30.7665 | 29.3014 | 27.9061 | 26.5772 | 25.3117 | 24.1063 | 22.9584 | 21.8652
|  | Both | Both | All | All | Both | Capital | Capital | Chlorination | Chlorine Pumps and Injector | 46300.9901 | $ | Year 1 | 25 | CAPDET, Pumps | Equipment + Installation | 46300.9901 | 46300.9901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46300.9901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | Both | All | Mixed WW | Capital | Capital | Chlorination | Contact Basin | 3360 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 3360 | 3360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | Both | All | Both | Energy | Electricity | Chlorination | Operational Electricity | 346.3624 | $/yr | Annual |  |  |  | 6001.8851 | 346.3624 | 346.3624 | 339.4352 | 339.4352 | 339.4352 | 346.3624 | 353.2897 | 367.1442 | 370.6078 | 370.6078 | 377.535 | 380.9987 | 380.9987 | 380.9987 | 384.4623 | 384.4623 | 387.9259 | 391.3895 | 391.3895 | 394.8532 | 398.3168 | 398.3168 | 401.7804 | 401.7804 | 405.244 | 408.7077 | 412.1713 | 415.6349 | 419.0985 | 422.5622 | 346.3624 | 329.869 | 307.8777 | 293.2169 | 279.2542 | 271.384 | 263.6302 | 260.9225 | 250.8419 | 238.8971 | 231.7738 | 222.762 | 212.1543 | 202.0517 | 194.1796 | 184.9329 | 177.7133 | 170.762 | 162.6304 | 156.2568 | 150.1214 | 142.9728 | 137.3486 | 130.8082 | 125.6532 | 120.6925 | 115.9194 | 111.3271 | 106.9094 | 102.6599
|  | Both | Both | All | All | Both | Materials | Materials | Chlorination | General Maintenance | 1608.2415 | $/yr | Annual |  |  |  | 25958.7442 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1531.6586 | 1458.7224 | 1389.2595 | 1323.1043 | 1260.0993 | 1200.0946 | 1142.9472 | 1088.5211 | 1036.6868 | 987.3208 | 940.3055 | 895.529 | 852.8848 | 812.2712 | 773.5917 | 736.754 | 701.6704 | 668.2576 | 636.4358 | 606.1293 | 577.266 | 549.7771 | 523.5973 | 498.6641 | 474.9182 | 452.303 | 430.7648 | 410.2522 | 390.7164
|  | Both | Sewered | Building | RVFW | Mixed WW | Chemical | Chemicals | Chlorination | Sodium Hypochlorite | 110.6957 | $/yr | Annual |  |  |  | 1786.747 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 110.6957 | 105.4244 | 100.4042 | 95.6231 | 91.0696 | 86.733 | 82.6028 | 78.6693 | 74.9232 | 71.3554 | 67.9575 | 64.7215 | 61.6395 | 58.7043 | 55.9088 | 53.2465 | 50.711 | 48.2962 | 45.9963 | 43.806 | 41.72 | 39.7334 | 37.8413 | 36.0393 | 34.3232 | 32.6887 | 31.1321 | 29.6496 | 28.2378 | 26.8931
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Clarification | Slant Plate Clarifier | 70950 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 70950 | 70950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | General | Clarification | General maintenance | 532.125 | $/yr | Annual |  |  |  | 8589.0688 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 506.7857 | 482.6531 | 459.6696 | 437.7806 | 416.9339 | 397.0799 | 378.1713 | 360.1631 | 343.0125 | 326.6786 | 311.1225 | 296.3071 | 282.1972 | 268.7593 | 255.9612 | 243.7726 | 232.1644 | 221.1089 | 210.5799 | 200.5523 | 191.0022 | 181.9069 | 173.2446 | 164.9949 | 157.138 | 149.6552 | 142.5288 | 135.7417 | 129.2778
|  | Both | Sewered | Building | All | Graywater | Capital | Capital | Chlorination | Contact Basin | 2474 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 2474 | 2474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All | Mixed WW | Materials | General | Chlorination | Basin Maintenance | 25.2 | $/yr | Annual |  |  |  | 406.7551 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 24 | 22.8571 | 21.7687 | 20.7321 | 19.7449 | 18.8046 | 17.9092 | 17.0564 | 16.2441 | 15.4706 | 14.7339 | 14.0323 | 13.3641 | 12.7277 | 12.1216 | 11.5444 | 10.9947 | 10.4711 | 9.9725 | 9.4976 | 9.0453 | 8.6146 | 8.2044 | 7.8137 | 7.4416 | 7.0873 | 6.7498 | 6.4284 | 6.1222
|  | Both | Sewered | Building | RVFW | Graywater | Chemical | Chemicals | Chlorination | Sodium Hypochlorite | 67.3932 | $/yr | Annual |  |  |  | 1087.7991 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 67.3932 | 64.184 | 61.1276 | 58.2168 | 55.4446 | 52.8044 | 50.2899 | 47.8951 | 45.6144 | 43.4423 | 41.3736 | 39.4034 | 37.5271 | 35.7401 | 34.0382 | 32.4173 | 30.8736 | 29.4034 | 28.0033 | 26.6698 | 25.3998 | 24.1903 | 23.0384 | 21.9413 | 20.8965 | 19.9014 | 18.9537 | 18.0512 | 17.1916 | 16.3729
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Clarification | Slant Plate Clarifier | 47300 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 47300 | 47300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | General | Clarification | General maintenance | 354.75 | $/yr | Annual |  |  |  | 5726.0459 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 337.8571 | 321.7687 | 306.4464 | 291.8537 | 277.9559 | 264.7199 | 252.1142 | 240.1088 | 228.675 | 217.7857 | 207.415 | 197.5381 | 188.1315 | 179.1729 | 170.6408 | 162.5151 | 154.7762 | 147.406 | 140.3866 | 133.7015 | 127.3348 | 121.2712 | 115.4964 | 109.9966 | 104.7587 | 99.7702 | 95.0192 | 90.4945 | 86.1852
|  | Both | Sewered | Building | RVFW | Graywater | Energy | Electricity | Wetland | Electricity | 1810.8478 | $/yr | Annual |  |  |  | 31378.983 | 1810.8478 | 1810.8478 | 1774.6309 | 1774.6309 | 1774.6309 | 1810.8478 | 1847.0648 | 1919.4987 | 1937.6072 | 1937.6072 | 1973.8241 | 1991.9326 | 1991.9326 | 1991.9326 | 2010.0411 | 2010.0411 | 2028.1496 | 2046.258 | 2046.258 | 2064.3665 | 2082.475 | 2082.475 | 2100.5835 | 2100.5835 | 2118.6919 | 2136.8004 | 2154.9089 | 2173.0174 | 2191.1259 | 2209.2343 | 1810.8478 | 1724.617 | 1609.6425 | 1532.9929 | 1459.9932 | 1418.8467 | 1378.3082 | 1364.1519 | 1311.4488 | 1248.9989 | 1211.7568 | 1164.6417 | 1109.1826 | 1056.3644 | 1015.2073 | 966.8641 | 929.1187 | 892.7756 | 850.2625 | 816.9399 | 784.8629 | 747.4885 | 718.0842 | 683.8897 | 656.9384 | 631.0031 | 606.0482 | 582.0391 | 558.9423 | 536.7254
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | HPDE Pipe | 42094 | $ | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 42094 | 42094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | Bed Concrete and Construction | 77798 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 77798 | 77798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | Gravel | 2357 | $ | Year 1 | 10 |  | Equipment + Installation | 2357 | 2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | Wood Chips | 571 | $ | Year 1 | 2 | RSMeans | Equipment + Installation | 571 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | Pumps | 84851 | $ | Year 1 | 25 | RSMeans for cost, Lifespan CAPDET | Equipment + Installation | 84851 | 84851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | Steel Grating | 40946 | $ | Replace at Lifespan | 40 | RSMeans for cost, Lifespan CAPDET | Equipment + Installation | 40946 | 40946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Maintenance Labor | Wetland | Wetland Maintenance Labor | 13892.9088 | $/yr | Annual |  | Gross et al. 2007a | For the wetland itself (i.e. not pumps) | 224246.4636 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13892.9088 | 13231.3417 | 12601.2778 | 12001.217 | 11429.7305 | 10885.4576 | 10367.1025 | 9873.4309 | 9403.2675 | 8955.4929 | 8529.0409 | 8122.8961 | 7736.0915 | 7367.7062 | 7016.863 | 6682.7267 | 6364.5016 | 6061.4301 | 5772.7906 | 5497.8958 | 5236.0912 | 4986.7535 | 4749.2891 | 4523.1325 | 4307.7452 | 4102.6145 | 3907.2519 | 3721.1923 | 3543.9926 | 3375.2311
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | Crushed Limestone | 917 | $ | Year 1 | 10 |  | Equipment + Installation | 917 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | Direct + Indirect | 296822 | $ | Year 1 |  |  | Direct and Indirect Cost | 296822 | 296822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | RVFW Effluent Storage | 8000 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 8000 | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | General | Wetland | Storage tank Maintanence | 60 | $/yr | Annual |  |  |  | 968.4644 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 57.1429 | 54.4218 | 51.8303 | 49.3621 | 47.0116 | 44.7729 | 42.6409 | 40.6104 | 38.6765 | 36.8348 | 35.0808 | 33.4102 | 31.8193 | 30.3041 | 28.861 | 27.4867 | 26.1778 | 24.9312 | 23.744 | 22.6134 | 21.5365 | 20.511 | 19.5343 | 18.6041 | 17.7182 | 16.8744 | 16.0709 | 15.3056 | 14.5768
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage | 8000 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 8000 | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | General | Building Reuse | Storage tank Maintanence | 60 | $/yr | Annual |  |  |  | 968.4644 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 57.1429 | 54.4218 | 51.8303 | 49.3621 | 47.0116 | 44.7729 | 42.6409 | 40.6104 | 38.6765 | 36.8348 | 35.0808 | 33.4102 | 31.8193 | 30.3041 | 28.861 | 27.4867 | 26.1778 | 24.9312 | 23.744 | 22.6134 | 21.5365 | 20.511 | 19.5343 | 18.6041 | 17.7182 | 16.8744 | 16.0709 | 15.3056 | 14.5768
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Equalization | Aerators | 40433.7165 | $ | Year 1 | 15 | CAPDET, Aerators | Equipment + Installation | 40433.7165 | 40433.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40433.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Equalization | Tank | 19352 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 19352 | 19352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Energy | Electricity | Equalization | Electricity | 1265.5401 | $/yr | Annual |  |  |  | 21929.7065 | 1265.5401 | 1265.5401 | 1240.2293 | 1240.2293 | 1240.2293 | 1265.5401 | 1290.8509 | 1341.4725 | 1354.1279 | 1354.1279 | 1379.4387 | 1392.0941 | 1392.0941 | 1392.0941 | 1404.7495 | 1404.7495 | 1417.4049 | 1430.0603 | 1430.0603 | 1442.7157 | 1455.3711 | 1455.3711 | 1468.0265 | 1468.0265 | 1480.6819 | 1493.3373 | 1505.9927 | 1518.6481 | 1531.3035 | 1543.9589 | 1265.5401 | 1205.2763 | 1124.9245 | 1071.3567 | 1020.3397 | 991.5838 | 963.2528 | 953.3595 | 916.5271 | 872.8829 | 846.8557 | 813.9286 | 775.1701 | 738.2572 | 709.494 | 675.7085 | 649.3295 | 623.9306 | 594.2196 | 570.9316 | 548.5141 | 522.3943 | 501.8447 | 477.9473 | 459.1119 | 440.9866 | 423.5465 | 406.7673 | 390.6258 | 375.0991
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Equalization | Aerators | 38250.5109 | $ | Year 1 | 15 | CAPDET, Aerators | Equipment + Installation | 38250.5109 | 38250.5109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38250.5109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Equalization | Tank | 14941 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 14941 | 14941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Energy | Electricity | Equalization | Electricity | 949.0098 | $/yr | Annual |  |  |  | 16444.7623 | 949.0098 | 949.0098 | 930.0296 | 930.0296 | 930.0296 | 949.0098 | 967.99 | 1005.9504 | 1015.4405 | 1015.4405 | 1034.4207 | 1043.9108 | 1043.9108 | 1043.9108 | 1053.4009 | 1053.4009 | 1062.891 | 1072.3811 | 1072.3811 | 1081.8712 | 1091.3613 | 1091.3613 | 1100.8514 | 1100.8514 | 1110.3414 | 1119.8315 | 1129.3216 | 1138.8117 | 1148.3018 | 1157.7919 | 949.0098 | 903.8188 | 843.5643 | 803.3945 | 765.1376 | 743.574 | 722.329 | 714.9101 | 687.2901 | 654.562 | 635.0446 | 610.353 | 581.2886 | 553.6082 | 532.039 | 506.7038 | 486.9226 | 467.8763 | 445.5965 | 428.1332 | 411.3226 | 391.7358 | 376.3259 | 358.4056 | 344.2813 | 330.6894 | 317.6112 | 305.0288 | 292.9245 | 281.2813
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | General | Equalization | Tank + Aerator | 1155.9829 | $/yr | Annual |  |  |  | 18658.8052 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1100.9361 | 1048.5106 | 998.5815 | 951.03 | 905.7429 | 862.6122 | 821.5355 | 782.4147 | 745.1569 | 709.6732 | 675.8793 | 643.6945 | 613.0424 | 583.8499 | 556.0475 | 529.5691 | 504.3515 | 480.3348 | 457.4617 | 435.6778 | 414.9312 | 395.1726 | 376.3549 | 358.4332 | 341.365 | 325.1095 | 309.6281 | 294.8839 | 280.8418
|  | Both | Sewered | Building | RVFW | Graywater | Materials | General | Equalization | Tank + Aerator | 1068.3203 | $/yr | Annual |  |  |  | 17243.8361 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1017.4479 | 968.998 | 922.8552 | 878.9097 | 837.0569 | 797.197 | 759.2353 | 723.0812 | 688.6488 | 655.856 | 624.6247 | 594.8807 | 566.553 | 539.5743 | 513.8803 | 489.4098 | 466.1046 | 443.9091 | 422.7706 | 402.6387 | 383.4654 | 365.2051 | 347.8144 | 331.2518 | 315.4779 | 300.4552 | 286.1478 | 272.5217 | 259.5445
|  | Both | Sewered | Building | All MBR | Mixed WW | Materials | Materials | UV | Bulbs | 125.9474 | $/replacement | Replace at Lifespan | 1 | Atlantic UV 2018 | Equipment + Installation | 1876.3799 | 0 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 125.9474 | 0 | 0 | 119.9499 | 114.238 | 108.7981 | 103.6172 | 98.6831 | 93.9839 | 89.5084 | 85.2461 | 81.1868 | 77.3208 | 73.6388 | 70.1322 | 66.7926 | 63.612 | 60.5828 | 57.6979 | 54.9504 | 52.3337 | 49.8417 | 47.4682 | 45.2078 | 43.0551 | 41.0048 | 39.0522 | 37.1926 | 35.4215 | 33.7348 | 32.1284 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Materials | Materials | UV | Quartz Sleeve | 100 | $/replacement | Replace at Lifespan | 5 | CAPDET, quartz sleeve | Equipment + Installation | 267.8181 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2702 | 0 | 0 | 0 | 0 | 64.4609 | 0 | 0 | 0 | 0 | 50.5068 | 0 | 0 | 0 | 0 | 39.5734 | 0 | 0 | 0 | 0 | 31.0068 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Capital | Capital | UV | UV System | 5064 | $/replacement | Replace at Lifespan | 30 | CAPDET, UV Strucutral | Equipment + Installation | 5064 | 5064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Materials | General | UV | General Maintenance | 37.98 | $/yr | Annual |  |  |  | 613.038 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 36.1714 | 34.449 | 32.8086 | 31.2462 | 29.7583 | 28.3413 | 26.9917 | 25.7064 | 24.4822 | 23.3164 | 22.2061 | 21.1487 | 20.1416 | 19.1825 | 18.269 | 17.3991 | 16.5705 | 15.7815 | 15.03 | 14.3143 | 13.6326 | 12.9835 | 12.3652 | 11.7764 | 11.2156 | 10.6815 | 10.1729 | 9.6885 | 9.2271
|  | Both | Sewered | Building | All MBR | Mixed WW | Energy | Electricity | UV | Operational Electricity | 91.6272 | $/yr | Annual |  |  |  | 1587.747 | 91.6272 | 91.6272 | 89.7947 | 89.7947 | 89.7947 | 91.6272 | 93.4597 | 97.1248 | 98.0411 | 98.0411 | 99.8736 | 100.7899 | 100.7899 | 100.7899 | 101.7062 | 101.7062 | 102.6225 | 103.5387 | 103.5387 | 104.455 | 105.3713 | 105.3713 | 106.2875 | 106.2875 | 107.2038 | 108.1201 | 109.0364 | 109.9526 | 110.8689 | 111.7852 | 91.6272 | 87.264 | 81.4464 | 77.568 | 73.8743 | 71.7923 | 69.7411 | 69.0248 | 66.3581 | 63.1982 | 61.3138 | 58.9298 | 56.1236 | 53.451 | 51.3685 | 48.9224 | 47.0125 | 45.1736 | 43.0225 | 41.3364 | 39.7133 | 37.8222 | 36.3344 | 34.6042 | 33.2405 | 31.9282 | 30.6655 | 29.4506 | 28.282 | 27.1578
|  | Both | Sewered | Building | AeMBR | Mixed WW | Chemical | Chemicals | Chlorination | Sodium Hypochlorite | 253.1058 | $/yr | Annual |  |  |  | 4085.3994 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 253.1058 | 241.0531 | 229.5744 | 218.6423 | 208.2308 | 198.315 | 188.8714 | 179.8776 | 171.312 | 163.1543 | 155.385 | 147.9857 | 140.9388 | 134.2274 | 127.8356 | 121.7482 | 115.9507 | 110.4292 | 105.1707 | 100.1626 | 95.3929 | 90.8504 | 86.5242 | 82.404 | 78.48 | 74.7428 | 71.1837 | 67.794 | 64.5657 | 61.4911
|  | Both | Sewered | Building | AeMBR | Graywater | Chemical | Chemicals | Chlorination | Sodium Hypochlorite | 143.9349 | $/yr | Annual |  |  |  | 2323.2633 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 143.9349 | 137.0808 | 130.5532 | 124.3363 | 118.4156 | 112.7767 | 107.4064 | 102.2918 | 97.4208 | 92.7817 | 88.3635 | 84.1557 | 80.1483 | 76.3317 | 72.6969 | 69.2351 | 65.9382 | 62.7983 | 59.8079 | 56.9599 | 54.2475 | 51.6643 | 49.2041 | 46.8611 | 44.6296 | 42.5044 | 40.4803 | 38.5527 | 36.7169 | 34.9684
|  | Both | Sewered | Building | AnMBR | Mixed WW | Chemical | Chemicals | Chlorination | Sodium Hypochlorite | 873.0625 | $/yr | Annual |  |  |  | 14092.1668 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 873.0625 | 831.4881 | 791.8935 | 754.1843 | 718.2707 | 684.0674 | 651.4927 | 620.4693 | 590.9231 | 562.7839 | 535.9847 | 510.4616 | 486.1539 | 463.0037 | 440.9559 | 419.958 | 399.96 | 380.9143 | 362.7755 | 345.5005 | 329.0481 | 313.3791 | 298.4563 | 284.2441 | 270.7087 | 257.8178 | 245.5408 | 233.8483 | 222.7127 | 212.1073
|  | Both | Sewered | Building | AnMBR | Graywater | Chemical | Chemicals | Chlorination | Sodium Hypochlorite | 260.4245 | $/yr | Annual |  |  |  | 4203.5314 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 260.4245 | 248.0234 | 236.2127 | 224.9645 | 214.2519 | 204.0494 | 194.3328 | 185.0788 | 176.2656 | 167.872 | 159.8781 | 152.2648 | 145.0141 | 138.1087 | 131.5321 | 125.2686 | 119.3035 | 113.6224 | 108.2118 | 103.0588 | 98.1513 | 93.4774 | 89.0261 | 84.7868 | 80.7493 | 76.9041 | 73.242 | 69.7543 | 66.4326 | 63.2692
|  | Both | Sewered | Building | All MBR | Mixed WW | Capital | Capital | Fine Screen | Construction | 31788.103 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 31788.103 | 31788.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31788.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Materials | Materials | Fine Screen | Maintenance | 794.7026 | $/yr | Annual |  |  |  | 12827.3527 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 756.8596 | 720.8187 | 686.494 | 653.8038 | 622.6703 | 593.0193 | 564.7803 | 537.886 | 512.2724 | 487.8784 | 464.6461 | 442.5201 | 421.4477 | 401.3788 | 382.2655 | 364.0624 | 346.7261 | 330.2153 | 314.4908 | 299.515 | 285.2524 | 271.669 | 258.7324 | 246.4118 | 234.6779 | 223.5027 | 212.8597 | 202.7236 | 193.0701
|  | Both | Sewered | Building | All MBR | Mixed WW | Labor | Operations Labor | Fine Screen | Operations Labor | 7989.6839 | $/yr | Annual |  |  |  | 128962.0762 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7989.6839 | 7609.2228 | 7246.8789 | 6901.7894 | 6573.1327 | 6260.1264 | 5962.0252 | 5678.1192 | 5407.7326 | 5150.2215 | 4904.9729 | 4671.4027 | 4448.955 | 4237.1 | 4035.3333 | 3843.1746 | 3660.1663 | 3485.8726 | 3319.8787 | 3161.7892 | 3011.2278 | 2867.836 | 2731.2724 | 2601.2118 | 2477.3446 | 2359.3758 | 2247.0246 | 2140.0234 | 2038.1175 | 1941.0643
|  | Both | Sewered | Building | All MBR | Graywater | Capital | Capital | Fine Screen | Construction | 24068.9192 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 24068.9192 | 24068.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24068.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Materials | Materials | Fine Screen | Maintenance | 601.723 | $/yr | Annual |  |  |  | 9712.4549 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 573.0695 | 545.7805 | 519.7909 | 495.039 | 471.4657 | 449.015 | 427.6333 | 407.2698 | 387.876 | 369.4057 | 351.815 | 335.0619 | 319.1065 | 303.911 | 289.439 | 275.6562 | 262.5297 | 250.0283 | 238.1222 | 226.7831 | 215.9839 | 205.6989 | 195.9037 | 186.575 | 177.6905 | 169.229 | 161.1705 | 153.4957 | 146.1864
|  | Both | Sewered | Building | All MBR | Graywater | Labor | Operations Labor | Fine Screen | Operations Labor | 7408.9154 | $/yr | Annual |  |  |  | 119587.8478 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7408.9154 | 7056.1099 | 6720.1046 | 6400.0996 | 6095.333 | 5805.079 | 5528.6467 | 5265.3778 | 5014.6455 | 4775.8529 | 4548.4313 | 4331.8394 | 4125.5613 | 3929.106 | 3742.0057 | 3563.815 | 3394.1095 | 3232.4852 | 3078.5574 | 2931.9594 | 2792.3423 | 2659.3736 | 2532.7368 | 2412.1302 | 2297.2669 | 2187.8732 | 2083.6888 | 1984.4655 | 1889.9672 | 1799.9687
|  | Both | Sewered | Building | All MBR | Mixed WW | Capital | Capital | Equalization | Aerators | 35419.7746 | $ | Year 1 | 15 | CAPDET, Aerators | Equipment + Installation | 35419.7746 | 35419.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35419.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Capital | Capital | Equalization | Tank | 15130 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 15130 | 15130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Energy | Electricity | Equalization | Electricity | 649.3327 | $/yr | Annual |  |  |  | 11251.8561 | 649.3327 | 649.3327 | 636.346 | 636.346 | 636.346 | 649.3327 | 662.3193 | 688.2926 | 694.786 | 694.786 | 707.7726 | 714.2659 | 714.2659 | 714.2659 | 720.7593 | 720.7593 | 727.2526 | 733.7459 | 733.7459 | 740.2393 | 746.7326 | 746.7326 | 753.2259 | 753.2259 | 759.7192 | 766.2126 | 772.7059 | 779.1992 | 785.6925 | 792.1859 | 649.3327 | 618.4121 | 577.1846 | 549.6996 | 523.5235 | 508.7691 | 494.2329 | 489.1567 | 470.2585 | 447.8652 | 434.511 | 417.6165 | 397.73 | 378.7905 | 364.0324 | 346.6975 | 333.1628 | 320.1309 | 304.8866 | 292.9378 | 281.4357 | 268.034 | 257.4902 | 245.2287 | 235.5646 | 226.2647 | 217.3164 | 208.7072 | 200.4252 | 192.4586
|  | Both | Sewered | Building | All MBR | Mixed WW | Materials | General | Equalization | Tank + Aerator | 998.9694 | $/yr | Annual |  |  |  | 16124.438 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 951.3994 | 906.0947 | 862.9473 | 821.8546 | 782.7186 | 745.4463 | 709.9489 | 676.1418 | 643.9446 | 613.2805 | 584.0767 | 556.2635 | 529.7748 | 504.5474 | 480.5213 | 457.6394 | 435.847 | 415.0924 | 395.3261 | 376.501 | 358.5724 | 341.4975 | 325.2358 | 309.7483 | 294.9984 | 280.9509 | 267.5723 | 254.8307 | 242.6959
|  | Both | Sewered | Building | All MBR | Mixed WW | Energy | Electricity | Fine Screen | Electricity | 561.5798 | $/yr | Annual |  |  |  | 9731.2443 | 561.5798 | 561.5798 | 550.3482 | 550.3482 | 550.3482 | 561.5798 | 572.8114 | 595.2746 | 600.8904 | 600.8904 | 612.122 | 617.7378 | 617.7378 | 617.7378 | 623.3536 | 623.3536 | 628.9694 | 634.5852 | 634.5852 | 640.201 | 645.8168 | 645.8168 | 651.4326 | 651.4326 | 657.0483 | 662.6641 | 668.2799 | 673.8957 | 679.5115 | 685.1273 | 561.5798 | 534.8379 | 499.182 | 475.4115 | 452.7728 | 440.0125 | 427.4407 | 423.0505 | 406.7063 | 387.3393 | 375.7898 | 361.1785 | 343.9795 | 327.5995 | 314.8359 | 299.8437 | 288.1381 | 276.8674 | 263.6832 | 253.3493 | 243.4015 | 231.811 | 222.6921 | 212.0877 | 203.7296 | 195.6866 | 187.9475 | 180.5018 | 173.3391 | 166.4492
|  | Both | Sewered | Building | All MBR | Graywater | Energy | Electricity | Fine Screen | Electricity | 454.4554 | $/yr | Annual |  |  |  | 7874.9566 | 454.4554 | 454.4554 | 445.3663 | 445.3663 | 445.3663 | 454.4554 | 463.5445 | 481.7227 | 486.2673 | 486.2673 | 495.3564 | 499.9009 | 499.9009 | 499.9009 | 504.4455 | 504.4455 | 508.99 | 513.5346 | 513.5346 | 518.0791 | 522.6237 | 522.6237 | 527.1683 | 527.1683 | 531.7128 | 536.2574 | 540.8019 | 545.3465 | 549.891 | 554.4356 | 454.4554 | 432.8147 | 403.9603 | 384.7241 | 366.4039 | 356.0777 | 345.904 | 342.3513 | 329.1248 | 313.4522 | 304.1058 | 292.2817 | 278.3635 | 265.1081 | 254.7792 | 242.6469 | 233.1742 | 224.0534 | 213.3842 | 205.0215 | 196.9714 | 187.5918 | 180.2124 | 171.6309 | 164.8671 | 158.3583 | 152.0955 | 146.0701 | 140.2737 | 134.6981
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Blowers | 23530 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 23530 | 23530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Membrane | 23559 | $ | Year 1 | 10 | CAPDET, membrane | Equipment + Installation | 23559 | 23559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Permeate Pumps | 23670 | $ | Year 1 | 25 | CAPDET, pumps | Equipment + Installation | 23670 | 23670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Swing Arms | 48669.2015 | $ | Year 1 | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 48669.2015 | 48669.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48669.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Tank | 27255 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 27255 | 27255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Minor Additional Costs | 16941 | $ | Year 1 |  |  | Equipment + Installation | 16941 | 16941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Direct + Indirect | 221664 | $ | Year 1 |  |  | Direct and Indirect Cost | 221664 | 221664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Diffusers | 2141 | $ | Year 1 | 10 | CADPET, fine diffuser | Equipment + Installation | 2141 | 2141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Air Piping, Installation, Ancillary | 16980 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 16980 | 16980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Blowers | 31345 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 31345 | 31345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Membrane | 47118 | $ | Year 1 | 10 | CAPDET, membrane | Equipment + Installation | 47118 | 47118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Permeate Pumps | 32115 | $ | Year 1 | 25 | CAPDET, pumps | Equipment + Installation | 32115 | 32115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Swing Arms | 57666 | $ | Year 1 | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 57666 | 57666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Tank | 42752 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 42752 | 42752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Minor Additional Costs | 22883 | $ | Year 1 |  |  | Equipment + Installation | 22883 | 22883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Direct + Indirect | 299417 | $ | Year 1 |  |  | Direct and Indirect Cost | 299417 | 299417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Diffusers | 3801 | $ | Year 1 | 10 | CADPET, fine diffuser | Equipment + Installation | 3801 | 3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Air Piping | 9176.1797 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 9176.1797 | 9176.1797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9176.1797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | All MBR | Mixed WW | Capital | Capital | Fine Screen | Construction | 48966.2232 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 48966.2232 | 48966.2232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48966.2232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | All MBR | Mixed WW | Materials | Materials | Fine Screen | Maintenance | 1224.1556 | $/yr | Annual |  |  |  | 19759.1853 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1165.8625 | 1110.3452 | 1057.4716 | 1007.1158 | 959.1579 | 913.4837 | 869.9845 | 828.5567 | 789.1016 | 751.5253 | 715.7384 | 681.6556 | 649.1958 | 618.2818 | 588.8398 | 560.7998 | 534.095 | 508.6619 | 484.4399 | 461.3714 | 439.4013 | 418.4774 | 398.5499 | 379.5714 | 361.4965 | 344.2824 | 327.888 | 312.2743 | 297.4041
|  | Both | Both | District | All MBR | Mixed WW | Labor | Operations Labor | Fine Screen | Operations Labor | 9266.1597 | $/yr | Annual |  |  |  | 149565.7651 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 9266.1597 | 8824.914 | 8404.68 | 8004.4571 | 7623.2925 | 7260.2786 | 6914.551 | 6585.2867 | 6271.7016 | 5973.0491 | 5688.6182 | 5417.7316 | 5159.7444 | 4914.0423 | 4680.0403 | 4457.1812 | 4244.9345 | 4042.7948 | 3850.2807 | 3666.934 | 3492.3181 | 3326.0173 | 3167.6355 | 3016.7957 | 2873.1388 | 2736.3226 | 2606.0216 | 2481.9253 | 2363.7384 | 2251.1794
|  | Both | Both | District | All MBR | Mixed WW | Energy | Electricity | Fine Screen | Electricity | 774.0851 | $/yr | Annual |  |  |  | 13413.6089 | 774.0851 | 774.0851 | 758.6034 | 758.6034 | 758.6034 | 774.0851 | 789.5668 | 820.5302 | 828.2711 | 828.2711 | 843.7528 | 851.4937 | 851.4937 | 851.4937 | 859.2345 | 859.2345 | 866.9754 | 874.7162 | 874.7162 | 882.4571 | 890.1979 | 890.1979 | 897.9388 | 897.9388 | 905.6796 | 913.4205 | 921.1613 | 928.9022 | 936.643 | 944.3839 | 774.0851 | 737.2239 | 688.0757 | 655.3102 | 624.1049 | 606.516 | 589.1869 | 583.1355 | 560.6065 | 533.9109 | 517.991 | 497.8507 | 474.1435 | 451.5653 | 433.9718 | 413.3065 | 397.1714 | 381.6358 | 363.4627 | 349.2182 | 335.5062 | 319.5297 | 306.9603 | 292.3431 | 280.8222 | 269.7356 | 259.0681 | 248.8049 | 238.9317 | 229.4346
|  | Both | Sewered | District | AeMBR | Mixed WW | Energy | Electricity | AeMBR | Electricity | 7622.2978 | $/yr | Annual |  |  |  | 132081.7527 | 7622.2978 | 7622.2978 | 7469.8519 | 7469.8519 | 7469.8519 | 7622.2978 | 7774.7438 | 8079.6357 | 8155.8587 | 8155.8587 | 8308.3046 | 8384.5276 | 8384.5276 | 8384.5276 | 8460.7506 | 8460.7506 | 8536.9736 | 8613.1965 | 8613.1965 | 8689.4195 | 8765.6425 | 8765.6425 | 8841.8655 | 8841.8655 | 8918.0884 | 8994.3114 | 9070.5344 | 9146.7574 | 9222.9804 | 9299.2033 | 7622.2978 | 7259.3313 | 6775.3758 | 6452.7389 | 6145.4656 | 5972.2698 | 5801.6335 | 5742.0462 | 5520.2062 | 5257.3392 | 5100.5783 | 4902.2596 | 4668.8187 | 4446.494 | 4273.254 | 4069.7657 | 3910.886 | 3757.9091 | 3578.9611 | 3438.6984 | 3303.6785 | 3146.3604 | 3022.5906 | 2878.6577 | 2765.213 | 2656.0451 | 2551.0038 | 2449.9436 | 2352.7236 | 2259.2072
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | Equalization | Aerators | 40433.7165 | $ | Year 1 | 15 | CAPDET, Aerators | Equipment + Installation | 40433.7165 | 40433.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40433.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | Equalization | Tank | 26537 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 26537 | 26537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Energy | Electricity | Equalization | Electricity | 1298.6654 | $/yr | Annual |  |  |  | 22503.7123 | 1298.6654 | 1298.6654 | 1272.6921 | 1272.6921 | 1272.6921 | 1298.6654 | 1324.6387 | 1376.5853 | 1389.5719 | 1389.5719 | 1415.5452 | 1428.5319 | 1428.5319 | 1428.5319 | 1441.5185 | 1441.5185 | 1454.5052 | 1467.4919 | 1467.4919 | 1480.4785 | 1493.4652 | 1493.4652 | 1506.4518 | 1506.4518 | 1519.4385 | 1532.4251 | 1545.4118 | 1558.3984 | 1571.3851 | 1584.3717 | 1298.6654 | 1236.8242 | 1154.3692 | 1099.3992 | 1047.0469 | 1017.5383 | 988.4658 | 978.3135 | 940.517 | 895.7305 | 869.022 | 835.233 | 795.46 | 757.581 | 728.0648 | 693.3951 | 666.3256 | 640.2618 | 609.7732 | 585.8756 | 562.8713 | 536.0679 | 514.9804 | 490.4575 | 471.1291 | 452.5294 | 434.6327 | 417.4144 | 400.8503 | 384.9173
|  | Both | Both | District | AeMBR | Mixed WW | Materials | General | Equalization | Tank + Aerator | 1209.8704 | $/yr | Annual |  |  |  | 19528.6073 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1152.2575 | 1097.3881 | 1045.1316 | 995.3634 | 947.9651 | 902.8239 | 859.8323 | 818.8879 | 779.8933 | 742.7555 | 707.3862 | 673.7011 | 641.6201 | 611.0668 | 581.9684 | 554.2556 | 527.8625 | 502.7261 | 478.7868 | 455.9874 | 434.2737 | 413.594 | 393.8991 | 375.142 | 357.2781 | 340.2648 | 324.0618 | 308.6302 | 293.9336
|  | Both | Sewered | District | AeMBR | Mixed WW | Chemical | Chemicals | Chlorination | Sodium Hypochlorite | 512.9204 | $/yr | Annual |  |  |  | 8279.0865 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 512.9204 | 488.4957 | 465.234 | 443.08 | 421.9809 | 401.8866 | 382.7491 | 364.523 | 347.1647 | 330.6331 | 314.8887 | 299.894 | 285.6133 | 272.0127 | 259.0597 | 246.7235 | 234.9748 | 223.7855 | 213.129 | 202.98 | 193.3143 | 184.1089 | 175.3418 | 166.9922 | 159.0402 | 151.4668 | 144.2541 | 137.3849 | 130.8427 | 124.6121
|  | Both | Both | District | AeMBR | Mixed WW | Chemical | Chemicals | AeMBR | Sodium Hypochlorite, membrane cleaning | 100.9374 | $/yr | Annual |  |  |  | 1629.2376 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 100.9374 | 96.1308 | 91.5532 | 87.1935 | 83.0414 | 79.0871 | 75.321 | 71.7343 | 68.3184 | 65.0651 | 61.9668 | 59.016 | 56.2057 | 53.5292 | 50.9802 | 48.5526 | 46.2406 | 44.0386 | 41.9416 | 39.9443 | 38.0422 | 36.2307 | 34.5054 | 32.8623 | 31.2974 | 29.8071 | 28.3877 | 27.0359 | 25.7485 | 24.5224
|  | Both | Sewered | Building | AeMBR | Mixed WW | Chemical | Chemicals | AeMBR | Sodium Hypochlorite, membrane cleaning | 50.6212 | $/yr | Annual |  |  |  | 817.0799 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 50.6212 | 48.2106 | 45.9149 | 43.7285 | 41.6462 | 39.663 | 37.7743 | 35.9755 | 34.2624 | 32.6309 | 31.077 | 29.5971 | 28.1878 | 26.8455 | 25.5671 | 24.3496 | 23.1901 | 22.0858 | 21.0341 | 20.0325 | 19.0786 | 18.1701 | 17.3048 | 16.4808 | 15.696 | 14.9486 | 14.2367 | 13.5588 | 12.9131 | 12.2982
|  | Both | Sewered | Building | AeMBR | Mixed WW | Energy | Electricity | AeMBR | Electricity | 4164.8725 | $/yr | Annual |  |  |  | 72170.3183 | 4164.8725 | 4164.8725 | 4081.575 | 4081.575 | 4081.575 | 4164.8725 | 4248.17 | 4414.7648 | 4456.4136 | 4456.4136 | 4539.711 | 4581.3597 | 4581.3597 | 4581.3597 | 4623.0085 | 4623.0085 | 4664.6572 | 4706.3059 | 4706.3059 | 4747.9546 | 4789.6034 | 4789.6034 | 4831.2521 | 4831.2521 | 4872.9008 | 4914.5495 | 4956.1983 | 4997.847 | 5039.4957 | 5081.1444 | 4164.8725 | 3966.5452 | 3702.1089 | 3525.818 | 3357.9219 | 3263.2866 | 3170.0498 | 3137.491 | 3016.2761 | 2872.6439 | 2786.9888 | 2678.6262 | 2551.0725 | 2429.5929 | 2334.9334 | 2223.7461 | 2136.9332 | 2053.3457 | 1955.5673 | 1878.9269 | 1805.1511 | 1719.1916 | 1651.5629 | 1572.9171 | 1510.9302 | 1451.2801 | 1393.8848 | 1338.6649 | 1285.5433 | 1234.4454
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | Materials | AeMBR | AeMBR Process | 11056.6688 | $/yr | Annual |  |  |  | 178466.5044 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 11056.6688 | 10530.1607 | 10028.7245 | 9551.1662 | 9096.3488 | 8663.1893 | 8250.6565 | 7857.7681 | 7483.5886 | 7127.2273 | 6787.8355 | 6464.6052 | 6156.7669 | 5863.5875 | 5584.3691 | 5318.4467 | 5065.1874 | 4823.988 | 4594.2743 | 4375.4993 | 4167.1422 | 3968.7068 | 3779.7208 | 3599.7341 | 3428.3182 | 3265.0649 | 3109.5857 | 2961.5101 | 2820.4859 | 2686.177
|  | Both | Sewered | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | AeMBR Process | 12494.1558 | $/yr | Annual |  |  |  | 201669.0888 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 12494.1558 | 11899.196 | 11332.5677 | 10792.9216 | 10278.9729 | 9789.498 | 9323.3315 | 8879.3633 | 8456.5365 | 8053.8443 | 7670.3279 | 7305.0742 | 6957.2135 | 6625.9176 | 6310.3977 | 6009.9026 | 5723.7168 | 5451.1588 | 5191.5798 | 4944.3617 | 4708.9159 | 4484.6818 | 4271.1256 | 4067.7386 | 3874.0368 | 3689.5589 | 3513.8656 | 3346.5386 | 3187.1797 | 3035.4092
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage | 20000 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 20000 | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Materials | General | Building Reuse | Storage tank Maintanence | 150 | $/yr | Annual |  |  |  | 2421.161 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 142.8571 | 136.0544 | 129.5756 | 123.4054 | 117.5289 | 111.9323 | 106.6022 | 101.5259 | 96.6913 | 92.087 | 87.7019 | 83.5256 | 79.5482 | 75.7602 | 72.1526 | 68.7167 | 65.4445 | 62.3281 | 59.3601 | 56.5334 | 53.8414 | 51.2775 | 48.8357 | 46.5102 | 44.2954 | 42.1861 | 40.1772 | 38.264 | 36.4419
|  | Both | Both | District | All MBR | Both | Materials | Materials | UV | Bulbs | 421.0526 | $/replacement | Replace at Lifespan | 1 | Atlantic UV 2018 | Equipment + Installation | 6272.8957 | 0 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 421.0526 | 0 | 0 | 401.0025 | 381.9071 | 363.7211 | 346.401 | 329.9058 | 314.196 | 299.2342 | 284.985 | 271.4143 | 258.4898 | 246.1808 | 234.4579 | 223.2932 | 212.6602 | 202.5335 | 192.8891 | 183.7039 | 174.9561 | 166.6248 | 158.6903 | 151.1336 | 143.9368 | 137.0827 | 130.5549 | 124.338 | 118.4172 | 112.7782 | 107.4078 | 0
|  | Both | Both | District | All MBR | Both | Materials | Materials | UV | Quartz Sleeve | 228 | $/replacement | Replace at Lifespan | 5 | CAPDET, quartz sleeve | Equipment + Installation | 610.6253 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.5762 | 0 | 0 | 0 | 0 | 146.9708 | 0 | 0 | 0 | 0 | 115.1555 | 0 | 0 | 0 | 0 | 90.2273 | 0 | 0 | 0 | 0 | 70.6955 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | All MBR | Both | Capital | Capital | UV | UV System | 10384 | $/replacement | Replace at Lifespan | 30 | CAPDET, UV Strucutral | Equipment + Installation | 10384 | 10384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | All MBR | Both | Materials | General | UV | General Maintenance | 77.88 | $/yr | Annual |  |  |  | 1257.0668 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 74.1714 | 70.6395 | 67.2757 | 64.0721 | 61.021 | 58.1153 | 55.3479 | 52.7122 | 50.2021 | 47.8116 | 45.5348 | 43.3665 | 41.3014 | 39.3347 | 37.4616 | 35.6777 | 33.9788 | 32.3607 | 30.8198 | 29.3522 | 27.9544 | 26.6233 | 25.3555 | 24.1481 | 22.9982 | 21.903 | 20.86 | 19.8667 | 18.9207
|  | Both | Both | District | All MBR | Both | Energy | Electricity | UV | Operational Electricity | 237.6883 | $/yr | Annual |  |  |  | 4118.7433 | 237.6883 | 237.6883 | 232.9345 | 232.9345 | 232.9345 | 237.6883 | 242.4421 | 251.9496 | 254.3265 | 254.3265 | 259.0803 | 261.4571 | 261.4571 | 261.4571 | 263.834 | 263.834 | 266.2109 | 268.5878 | 268.5878 | 270.9647 | 273.3416 | 273.3416 | 275.7184 | 275.7184 | 278.0953 | 280.4722 | 282.8491 | 285.226 | 287.6028 | 289.9797 | 237.6883 | 226.3698 | 211.2785 | 201.2176 | 191.6358 | 186.235 | 180.914 | 179.0559 | 172.1382 | 163.9411 | 159.0528 | 152.8686 | 145.5891 | 138.6563 | 133.2541 | 126.9087 | 121.9543 | 117.184 | 111.6038 | 107.2299 | 103.0196 | 98.1139 | 94.2543 | 89.766 | 86.2284 | 82.8242 | 79.5487 | 76.3973 | 73.3657 | 70.4495
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | UV | Bulbs | 70.1754 | $/replacement | Replace at Lifespan | 1 | Atlantic UV 2018 | Equipment + Installation | 1045.4826 | 0 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 0 | 0 | 66.8338 | 63.6512 | 60.6202 | 57.7335 | 54.9843 | 52.366 | 49.8724 | 47.4975 | 45.2357 | 43.0816 | 41.0301 | 39.0763 | 37.2155 | 35.4434 | 33.7556 | 32.1482 | 30.6173 | 29.1593 | 27.7708 | 26.4484 | 25.1889 | 23.9895 | 22.8471 | 21.7592 | 20.723 | 19.7362 | 18.7964 | 17.9013 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | UV | Quartz Sleeve | 82 | $/replacement | Replace at Lifespan | 5 | CAPDET, quartz sleeve | Equipment + Installation | 219.6109 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.4616 | 0 | 0 | 0 | 0 | 52.8579 | 0 | 0 | 0 | 0 | 41.4156 | 0 | 0 | 0 | 0 | 32.4502 | 0 | 0 | 0 | 0 | 25.4256 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | UV | UV System | 4168 | $/replacement | Replace at Lifespan | 30 | CAPDET, UV Strucutral | Equipment + Installation | 4168 | 4168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | General | UV | General Maintenance | 31.26 | $/yr | Annual |  |  |  | 504.57 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 29.7714 | 28.3537 | 27.0036 | 25.7177 | 24.493 | 23.3267 | 22.2159 | 21.158 | 20.1505 | 19.1909 | 18.2771 | 17.4067 | 16.5778 | 15.7884 | 15.0366 | 14.3206 | 13.6386 | 12.9892 | 12.3706 | 11.7816 | 11.2205 | 10.6862 | 10.1774 | 9.6927 | 9.2312 | 8.7916 | 8.3729 | 7.9742 | 7.5945
|  | Both | Sewered | Building | AeMBR | Graywater | Energy | Electricity | UV | Operational Electricity | 74.774 | $/yr | Annual |  |  |  | 1295.709 | 74.774 | 74.774 | 73.2785 | 73.2785 | 73.2785 | 74.774 | 76.2695 | 79.2604 | 80.0082 | 80.0082 | 81.5036 | 82.2514 | 82.2514 | 82.2514 | 82.9991 | 82.9991 | 83.7469 | 84.4946 | 84.4946 | 85.2423 | 85.9901 | 85.9901 | 86.7378 | 86.7378 | 87.4856 | 88.2333 | 88.981 | 89.7288 | 90.4765 | 91.2243 | 74.774 | 71.2133 | 66.4658 | 63.3007 | 60.2864 | 58.5874 | 56.9135 | 56.3289 | 54.1527 | 51.574 | 50.0362 | 48.0907 | 45.8007 | 43.6197 | 41.9202 | 39.924 | 38.3654 | 36.8647 | 35.1093 | 33.7333 | 32.4088 | 30.8655 | 29.6513 | 28.2393 | 27.1265 | 26.0555 | 25.0251 | 24.0337 | 23.08 | 22.1626
|  | Both | Sewered | Building | All MBR | Graywater | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage | 8000 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 8000 | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Materials | General | Building Reuse | Storage tank Maintanence | 60 | $/yr | Annual |  |  |  | 968.4644 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 57.1429 | 54.4218 | 51.8303 | 49.3621 | 47.0116 | 44.7729 | 42.6409 | 40.6104 | 38.6765 | 36.8348 | 35.0808 | 33.4102 | 31.8193 | 30.3041 | 28.861 | 27.4867 | 26.1778 | 24.9312 | 23.744 | 22.6134 | 21.5365 | 20.511 | 19.5343 | 18.6041 | 17.7182 | 16.8744 | 16.0709 | 15.3056 | 14.5768
|  | Both | Sewered | Building | All MBR | Graywater | Capital | Capital | Equalization | Aerators | 33146.5444 | $ | Year 1 | 15 | CAPDET, Aerators | Equipment + Installation | 33146.5444 | 33146.5444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33146.5444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Capital | Capital | Equalization | Tank | 11528 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 11528 | 11528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Energy | Electricity | Equalization | Electricity | 454.4554 | $/yr | Annual |  |  |  | 7874.9566 | 454.4554 | 454.4554 | 445.3663 | 445.3663 | 445.3663 | 454.4554 | 463.5445 | 481.7227 | 486.2673 | 486.2673 | 495.3564 | 499.9009 | 499.9009 | 499.9009 | 504.4455 | 504.4455 | 508.99 | 513.5346 | 513.5346 | 518.0791 | 522.6237 | 522.6237 | 527.1683 | 527.1683 | 531.7128 | 536.2574 | 540.8019 | 545.3465 | 549.891 | 554.4356 | 454.4554 | 432.8147 | 403.9603 | 384.7241 | 366.4039 | 356.0777 | 345.904 | 342.3513 | 329.1248 | 313.4522 | 304.1058 | 292.2817 | 278.3635 | 265.1081 | 254.7792 | 242.6469 | 233.1742 | 224.0534 | 213.3842 | 205.0215 | 196.9714 | 187.5918 | 180.2124 | 171.6309 | 164.8671 | 158.3583 | 152.0955 | 146.0701 | 140.2737 | 134.6981
|  | Both | Sewered | Building | All MBR | Graywater | Materials | General | Equalization | Tank + Aerator | 915.1236 | $/yr | Annual |  |  |  | 14771.0775 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 871.5463 | 830.0441 | 790.5182 | 752.8745 | 717.0233 | 682.8793 | 650.3613 | 619.3917 | 589.8968 | 561.8065 | 535.0538 | 509.5751 | 485.3096 | 462.1996 | 440.1901 | 419.2287 | 399.2654 | 380.2528 | 362.1455 | 344.9005 | 328.4766 | 312.8349 | 297.938 | 283.7505 | 270.2385 | 257.37 | 245.1143 | 233.4422 | 222.3259
|  | Both | Sewered | Building | AeMBR | Graywater | Energy | Electricity | AeMBR | Electricity | 1830.9942 | $/yr | Annual |  |  |  | 31728.086 | 1830.9942 | 1830.9942 | 1794.3743 | 1794.3743 | 1794.3743 | 1830.9942 | 1867.6141 | 1940.8538 | 1959.1638 | 1959.1638 | 1995.7837 | 2014.0936 | 2014.0936 | 2014.0936 | 2032.4035 | 2032.4035 | 2050.7135 | 2069.0234 | 2069.0234 | 2087.3334 | 2105.6433 | 2105.6433 | 2123.9532 | 2123.9532 | 2142.2632 | 2160.5731 | 2178.8831 | 2197.193 | 2215.503 | 2233.8129 | 1830.9942 | 1743.804 | 1627.5504 | 1550.048 | 1476.2362 | 1434.6319 | 1393.6424 | 1379.3286 | 1326.0392 | 1262.8944 | 1225.238 | 1177.5988 | 1121.5227 | 1068.1168 | 1026.5019 | 977.6209 | 939.4555 | 902.7081 | 859.722 | 826.0287 | 793.5948 | 755.8046 | 726.0731 | 691.4982 | 664.2471 | 638.0232 | 612.7907 | 588.5145 | 565.1607 | 542.6966
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Blowers | 13680 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 13680 | 13680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Membrane | 15078 | $ | Year 1 | 10 | CAPDET, membrane | Equipment + Installation | 15078 | 15078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Permeate Pumps | 19440 | $ | Year 1 | 25 | CAPDET, pumps | Equipment + Installation | 19440 | 19440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Swing Arms | 48669.2015 | $ | Year 1 | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 48669.2015 | 48669.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48669.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Tank | 20765 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 20765 | 20765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Minor Additional Costs | 13603.9053 | $ | Year 1 |  |  | Equipment + Installation | 13603.9053 | 13603.9053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13603.9053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Direct + Indirect | 178000 | $ | Year 1 |  |  | Direct and Indirect Cost | 178000 | 178000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Diffusers | 848 | $ | Year 1 | 10 | CADPET, fine diffuser | Equipment + Installation | 848 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Air Piping, Installation, Ancillary | 15212 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 15212 | 15212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Chemical | Chemicals | AeMBR | Sodium Hypochlorite, membrane cleaning | 32.3244 | $/yr | Annual |  |  |  | 521.7498 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 32.3244 | 30.7851 | 29.3191 | 27.923 | 26.5933 | 25.327 | 24.1209 | 22.9723 | 21.8784 | 20.8366 | 19.8444 | 18.8994 | 17.9994 | 17.1423 | 16.326 | 15.5486 | 14.8082 | 14.103 | 13.4314 | 12.7918 | 12.1827 | 11.6026 | 11.0501 | 10.5239 | 10.0227 | 9.5455 | 9.0909 | 8.658 | 8.2457 | 7.8531
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | AeMBR | AeMBR Process | 10776.0859 | $/yr | Annual |  |  |  | 173937.5952 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10776.0859 | 10262.9389 | 9774.2276 | 9308.7882 | 8865.5125 | 8443.3453 | 8041.2812 | 7658.3631 | 7293.6791 | 6946.361 | 6615.5819 | 6300.5542 | 6000.5278 | 5714.7884 | 5442.6556 | 5183.4816 | 4936.6491 | 4701.5706 | 4477.6863 | 4264.4631 | 4061.3934 | 3867.9938 | 3683.8036 | 3508.3844 | 3341.3184 | 3182.208 | 3030.6743 | 2886.3565 | 2748.9109 | 2618.0104
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | Equalization | Aerators | 36773.6231 | $ | Year 1 | 15 | CAPDET, Aerators | Equipment + Installation | 36773.6231 | 36773.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36773.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | Equalization | Tank | 19987 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 19987 | 19987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Energy | Electricity | Equalization | Electricity | 788.8075 | $/yr | Annual |  |  |  | 13668.7226 | 788.8075 | 788.8075 | 773.0313 | 773.0313 | 773.0313 | 788.8075 | 804.5836 | 836.1359 | 844.024 | 844.024 | 859.8002 | 867.6882 | 867.6882 | 867.6882 | 875.5763 | 875.5763 | 883.4644 | 891.3525 | 891.3525 | 899.2405 | 907.1286 | 907.1286 | 915.0167 | 915.0167 | 922.9048 | 930.7928 | 938.6809 | 946.569 | 954.4571 | 962.3451 | 788.8075 | 751.2452 | 701.1622 | 667.7735 | 635.9748 | 618.0513 | 600.3927 | 594.2262 | 571.2687 | 544.0654 | 527.8427 | 507.3193 | 483.1613 | 460.1536 | 442.2255 | 421.1672 | 404.7252 | 388.8941 | 370.3754 | 355.86 | 341.8872 | 325.6069 | 312.7983 | 297.9032 | 286.1631 | 274.8657 | 263.9953 | 253.5369 | 243.4759 | 233.7982
|  | Both | Sewered | District | AeMBR | Graywater | Materials | General | Equalization | Tank + Aerator | 1069.2431 | $/yr | Annual |  |  |  | 17258.7312 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1018.3267 | 969.835 | 923.6524 | 879.6689 | 837.7799 | 797.8856 | 759.8911 | 723.7058 | 689.2436 | 656.4225 | 625.1643 | 595.3946 | 567.0424 | 540.0404 | 514.3242 | 489.8326 | 466.5072 | 444.2926 | 423.1358 | 402.9865 | 383.7966 | 365.5206 | 348.1149 | 331.538 | 315.7504 | 300.7147 | 286.395 | 272.7571 | 259.7687
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage | 16000 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 16000 | 16000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Materials | General | Building Reuse | Storage tank Maintanence | 120 | $/yr | Annual |  |  |  | 1936.9288 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 114.2857 | 108.8435 | 103.6605 | 98.7243 | 94.0231 | 89.5458 | 85.2818 | 81.2207 | 77.3531 | 73.6696 | 70.1615 | 66.8205 | 63.6386 | 60.6082 | 57.7221 | 54.9734 | 52.3556 | 49.8625 | 47.4881 | 45.2267 | 43.0731 | 41.022 | 39.0686 | 37.2081 | 35.4363 | 33.7489 | 32.1418 | 30.6112 | 29.1536
|  | Both | Sewered | District | All MBR | Graywater | Capital | Capital | Fine Screen | Construction | 36349.1574 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 36349.1574 | 36349.1574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36349.1574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | All MBR | Graywater | Materials | Materials | Fine Screen | Maintenance | 908.7289 | $/yr | Annual |  |  |  | 14667.8606 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 865.4561 | 824.2439 | 784.9942 | 747.6135 | 712.0129 | 678.1075 | 645.8167 | 615.0635 | 585.7748 | 557.8807 | 531.315 | 506.0143 | 481.9184 | 458.9699 | 437.1142 | 416.2992 | 396.4754 | 377.5956 | 359.6149 | 342.4904 | 326.1813 | 310.6489 | 295.8561 | 281.7677 | 268.3502 | 255.5716 | 243.4015 | 231.811 | 220.7724
|  | Both | Sewered | District | All MBR | Graywater | Labor | Operations Labor | Fine Screen | Operations Labor | 8615.9777 | $/yr | Annual |  |  |  | 139071.1298 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8615.9777 | 8205.693 | 7814.9457 | 7442.8055 | 7088.3862 | 6750.844 | 6429.3752 | 6123.2145 | 5831.6328 | 5553.936 | 5289.4629 | 5037.5837 | 4797.6988 | 4569.2369 | 4351.6542 | 4144.4326 | 3947.0787 | 3759.1225 | 3580.1167 | 3409.6349 | 3247.2714 | 3092.6394 | 2945.3709 | 2805.1151 | 2671.5382 | 2544.3221 | 2423.1639 | 2307.7751 | 2197.8811 | 2093.2201
|  | Both | Sewered | District | All MBR | Graywater | Energy | Electricity | Fine Screen | Electricity | 620.2754 | $/yr | Annual |  |  |  | 10748.3423 | 620.2754 | 620.2754 | 607.8699 | 607.8699 | 607.8699 | 620.2754 | 632.6809 | 657.492 | 663.6947 | 663.6947 | 676.1002 | 682.303 | 682.303 | 682.303 | 688.5057 | 688.5057 | 694.7085 | 700.9112 | 700.9112 | 707.114 | 713.3167 | 713.3167 | 719.5195 | 719.5195 | 725.7223 | 731.925 | 738.1278 | 744.3305 | 750.5333 | 756.736 | 620.2754 | 590.7385 | 551.3559 | 525.1009 | 500.0961 | 486.002 | 472.1163 | 467.2673 | 449.2147 | 427.8235 | 415.0669 | 398.9284 | 379.9318 | 361.8398 | 347.7422 | 331.183 | 318.254 | 305.8053 | 291.2431 | 279.829 | 268.8416 | 256.0396 | 245.9676 | 234.2549 | 225.0232 | 216.1395 | 207.5916 | 199.3677 | 191.4563 | 183.8462
|  | Both | Sewered | District | AeMBR | Graywater | Energy | Electricity | AeMBR | Electricity | 3648.0409 | $/yr | Annual |  |  |  | 63214.4853 | 3648.0409 | 3648.0409 | 3575.0801 | 3575.0801 | 3575.0801 | 3648.0409 | 3721.0017 | 3866.9233 | 3903.4037 | 3903.4037 | 3976.3646 | 4012.845 | 4012.845 | 4012.845 | 4049.3254 | 4049.3254 | 4085.8058 | 4122.2862 | 4122.2862 | 4158.7666 | 4195.247 | 4195.247 | 4231.7274 | 4231.7274 | 4268.2078 | 4304.6882 | 4341.1686 | 4377.6491 | 4414.1295 | 4450.6099 | 3648.0409 | 3474.3246 | 3242.703 | 3088.2886 | 2941.2272 | 2858.3355 | 2776.6688 | 2748.1502 | 2641.9773 | 2516.1689 | 2441.1429 | 2346.2273 | 2234.5022 | 2128.0974 | 2045.1845 | 1947.7947 | 1871.7547 | 1798.5398 | 1712.8951 | 1645.7652 | 1581.1445 | 1505.8519 | 1446.6155 | 1377.729 | 1323.4343 | 1271.1864 | 1220.9135 | 1172.5459 | 1126.0163 | 1081.2593
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Blowers | 20051 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 20051 | 20051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Membrane | 29213 | $ | Year 1 | 10 | CAPDET, membrane | Equipment + Installation | 29213 | 29213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Permeate Pumps | 26010 | $ | Year 1 | 25 | CAPDET, pumps | Equipment + Installation | 26010 | 26010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Swing Arms | 57434 | $ | Year 1 | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 57434 | 57434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Tank | 31536 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 31536 | 31536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Minor Additional Costs | 17650 | $ | Year 1 |  |  | Equipment + Installation | 17650 | 17650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Direct + Indirect | 230938 | $ | Year 1 |  |  | Direct and Indirect Cost | 230938 | 230938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Diffusers | 1483 | $ | Year 1 | 10 | CADPET, fine diffuser | Equipment + Installation | 1483 | 1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Air Piping | 7627.1772 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 7627.1772 | 7627.1772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7627.1772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Chemical | Chemicals | AeMBR | Sodium Hypochlorite, membrane cleaning | 62.819 | $/yr | Annual |  |  |  | 1013.9666 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 62.819 | 59.8276 | 56.9787 | 54.2654 | 51.6814 | 49.2204 | 46.8765 | 44.6443 | 42.5184 | 40.4937 | 38.5654 | 36.729 | 34.98 | 33.3143 | 31.7279 | 30.217 | 28.7781 | 27.4077 | 26.1026 | 24.8596 | 23.6758 | 22.5484 | 21.4747 | 20.4521 | 19.4782 | 18.5506 | 17.6673 | 16.826 | 16.0247 | 15.2617
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | AeMBR | AeMBR Process | 11220.7279 | $/yr | Annual |  |  |  | 181114.5941 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 11220.7279 | 10686.4075 | 10177.5309 | 9692.8866 | 9231.3206 | 8791.7339 | 8373.0799 | 7974.3618 | 7594.6303 | 7232.9812 | 6888.5536 | 6560.5272 | 6248.1211 | 5950.5916 | 5667.2301 | 5397.362 | 5140.3447 | 4895.5664 | 4662.4442 | 4440.423 | 4228.9743 | 4027.5946 | 3835.8044 | 3653.147 | 3479.1876 | 3313.512 | 3155.7258 | 3005.4531 | 2862.3363 | 2726.0346
|  | Both | Sewered | Building | AeMBR | Graywater | Labor | Operations Labor | Chlorination | Operations Labor | 1255.4977 | $/yr | Annual |  |  |  | 20265.0806 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1255.4977 | 1195.7121 | 1138.7734 | 1084.5461 | 1032.9011 | 983.7153 | 936.8717 | 892.2588 | 849.7703 | 809.305 | 770.7667 | 734.0635 | 699.1081 | 665.8172 | 634.1116 | 603.9159 | 575.158 | 547.7695 | 521.6852 | 496.8431 | 473.1839 | 450.6513 | 429.1917 | 408.754 | 389.2895 | 370.7519 | 353.0971 | 336.2829 | 320.2695 | 305.0185
|  | Both | Sewered | Building | AeMBR | Mixed WW | Labor | Operations Labor | Chlorination | Operations Labor | 1693.8369 | $/yr | Annual |  |  |  | 27340.3461 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1693.8369 | 1613.178 | 1536.36 | 1463.2 | 1393.5238 | 1327.1655 | 1263.9672 | 1203.7783 | 1146.4555 | 1091.8624 | 1039.8689 | 990.3514 | 943.1918 | 898.2779 | 855.5027 | 814.7645 | 775.9662 | 739.0154 | 703.8242 | 670.3088 | 638.3893 | 607.9898 | 579.0379 | 551.4647 | 525.2045 | 500.1947 | 476.3759 | 453.6914 | 432.087 | 411.5114
|  | Both | Sewered | Building | AnMBR | Graywater | Labor | Operations Labor | Chlorination | Operations Labor | 1719.7565 | $/yr | Annual |  |  |  | 27758.7169 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1719.7565 | 1637.8634 | 1559.8699 | 1485.5904 | 1414.848 | 1347.4742 | 1283.3088 | 1222.1989 | 1163.9989 | 1108.5704 | 1055.7813 | 1005.506 | 957.6248 | 912.0236 | 868.5939 | 827.2323 | 787.8403 | 750.3241 | 714.5944 | 680.5661 | 648.1582 | 617.2935 | 587.8986 | 559.9034 | 533.2413 | 507.8489 | 483.6656 | 460.6339 | 438.699 | 417.8085
|  | Both | Sewered | Building | AnMBR | Mixed WW | Labor | Operations Labor | Chlorination | Operations Labor | 3272.3053 | $/yr | Annual |  |  |  | 52818.5209 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3272.3053 | 3116.4813 | 2968.0774 | 2826.7404 | 2692.1337 | 2563.9368 | 2441.8446 | 2325.5663 | 2214.825 | 2109.3572 | 2008.9116 | 1913.2491 | 1822.142 | 1735.3734 | 1652.7365 | 1574.0348 | 1499.0808 | 1427.696 | 1359.7104 | 1294.9623 | 1233.2975 | 1174.569 | 1118.6372 | 1065.3687 | 1014.6369 | 966.3208 | 920.3056 | 876.4815 | 834.7443 | 794.9945
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Operations Labor | Chlorination | Operations Labor | 839.3416 | $/yr | Annual |  |  |  | 13547.8749 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 839.3416 | 799.373 | 761.3076 | 725.0549 | 690.5284 | 657.6461 | 626.3296 | 596.5044 | 568.0994 | 541.0471 | 515.2829 | 490.7457 | 467.3768 | 445.1208 | 423.9246 | 403.7377 | 384.5121 | 366.202 | 348.7638 | 332.156 | 316.339 | 301.2753 | 286.9288 | 273.2655 | 260.2529 | 247.8599 | 236.0571 | 224.8162 | 214.1107 | 203.915
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Operations Labor | Chlorination | Operations Labor | 1091.4578 | $/yr | Annual |  |  |  | 17617.3012 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1091.4578 | 1039.4837 | 989.9844 | 942.8423 | 897.9451 | 855.1858 | 814.4626 | 775.6787 | 738.7416 | 703.5635 | 670.0604 | 638.1528 | 607.7646 | 578.8234 | 551.2604 | 525.0099 | 500.0094 | 476.1994 | 453.5233 | 431.9269 | 411.359 | 391.7705 | 373.1147 | 355.3474 | 338.426 | 322.3105 | 306.9624 | 292.3451 | 278.4239 | 265.1657
|  | Both | Sewered | Building | AnMBR | Mixed WW | Energy | Electricity | AnMBR | Operation Energy | 5403.7878 | $/yr | Annual |  |  |  | 93638.6605 | 5403.7878 | 5403.7878 | 5295.712 | 5295.712 | 5295.712 | 5403.7878 | 5511.8635 | 5728.015 | 5782.0529 | 5782.0529 | 5890.1286 | 5944.1665 | 5944.1665 | 5944.1665 | 5998.2044 | 5998.2044 | 6052.2423 | 6106.2802 | 6106.2802 | 6160.318 | 6214.3559 | 6214.3559 | 6268.3938 | 6268.3938 | 6322.4317 | 6376.4695 | 6430.5074 | 6484.5453 | 6538.5832 | 6592.6211 | 5403.7878 | 5146.4645 | 4803.3669 | 4574.6351 | 4356.7954 | 4234.0091 | 4113.0374 | 4070.7933 | 3913.521 | 3727.1628 | 3616.028 | 3475.4311 | 3309.9343 | 3152.3184 | 3029.5008 | 2885.2389 | 2772.6019 | 2664.1498 | 2537.2855 | 2437.847 | 2342.1254 | 2230.5956 | 2142.8496 | 2040.8092 | 1960.3832 | 1882.9891 | 1808.5206 | 1736.8746 | 1667.951 | 1601.653
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | AnMBR | membrane | 62823.7722 | $ | Year 1 | 10 | CAPDET, membrane | Equipment + Installation | 62823.7722 | 62823.7722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62823.7722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | AnMBR | Permeate Pumps | 23670 | $ | Year 1 | 25 | CAPDET, Pumps | Equipment + Installation | 23670 | 23670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | AnMBR | Sludge Pump | 2592 | $ | Year 1 | 25 | CAPDET, Pumps | Equipment + Installation | 2592 | 2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | AnMBR | Biogas Recirculation Blower | 24595 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 24595 | 24595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | AnMBR | Anaerobic reactor and membrane tank | 48677 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 48677 | 48677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | AnMBR | Piping (AnReactor and Membrane tank) | 25131 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 25131 | 25131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | AnMBR | Mixers | 17455 | $ | Year 1 | 15 | CAPDET, process equipment | Equipment + Installation | 17455 | 17455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Both | Capital | Capital | AnMBR | Gas Safety Equipment | 53426 | $ | Year 1 | 15 | CAPDET, process equipment | Equipment + Installation | 53426 | 53426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | AeMBR | Sludge Pump | 3606 | $ | Year 1 | 25 | CAPDET, Pumps | Equipment + Installation | 3606 | 3606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | Zeolite | Adsorption Vessel - Steel | 60420.0449 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 60420.0449 | 60420.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60420.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | Zeolite | Feed System (pumps and piping | 15372.0212 | $ | Year 1 | 25 | CAPDET, pumps | Equipment + Installation | 15372.0212 | 15372.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15372.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | Zeolite | Regeneration System | 19265.0881 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 19265.0881 | 19265.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19265.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | Zeolite | Zeolite Replacement System | 27632.3545 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 27632.3545 | 27632.3545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27632.3545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | Zeolite | Misc., Direct, and Indirect Install Cost | 223749 | $ | Year 1 |  |  | Direct and Indirect Cost | 223749 | 223749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Chemical | Materials | Zeolite | Zeolite | 3425.8889 | $/yr | Annual |  |  |  | 55297.5253 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3425.8889 | 3262.7514 | 3107.3823 | 2959.4117 | 2818.4873 | 2684.2736 | 2556.4511 | 2434.7153 | 2318.7765 | 2208.3586 | 2103.1986 | 2003.0463 | 1907.6631 | 1816.822 | 1730.3067 | 1647.9112 | 1569.4392 | 1494.704 | 1423.5276 | 1355.7406 | 1291.1815 | 1229.6967 | 1171.1397 | 1115.3711 | 1062.2582 | 1011.6745 | 963.4995 | 917.6186 | 873.9225 | 832.3071
|  | Both | Sewered | Building | AnMBR | Mixed WW | Chemical | Chemicals | Zeolite | NaCl | 313.7463 | $/yr | Annual |  |  |  | 5064.2029 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 313.7463 | 298.806 | 284.5772 | 271.0259 | 258.1199 | 245.8285 | 234.1224 | 222.9737 | 212.3559 | 202.2437 | 192.613 | 183.441 | 174.7057 | 166.3864 | 158.4632 | 150.9174 | 143.7308 | 136.8865 | 130.3681 | 124.1601 | 118.2477 | 112.6169 | 107.2541 | 102.1468 | 97.2827 | 92.6502 | 88.2383 | 84.0364 | 80.0347 | 76.2235
|  | Both | Sewered | Building | AnMBR | Mixed WW | Chemical | Chemicals | Zeolite | NaOH | 3108.7694 | $/yr | Annual |  |  |  | 50178.8761 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 3108.7694 | 2960.7328 | 2819.7455 | 2685.4719 | 2557.5923 | 2435.8022 | 2319.8116 | 2209.3444 | 2104.1375 | 2003.9405 | 1908.5148 | 1817.6331 | 1731.0791 | 1648.6468 | 1570.1398 | 1495.3712 | 1424.1631 | 1356.3458 | 1291.7579 | 1230.2456 | 1171.6625 | 1115.869 | 1062.7324 | 1012.1261 | 963.9296 | 918.0282 | 874.3126 | 832.6787 | 793.0273 | 755.2641
|  | Both | Sewered | Building | AnMBR | Mixed WW | Energy | Electricity | Zeolite | Electricity | 303.6535 | $/yr | Annual |  |  |  | 5261.8104 | 303.6535 | 303.6535 | 297.5804 | 297.5804 | 297.5804 | 303.6535 | 309.7266 | 321.8727 | 324.9092 | 324.9092 | 330.9823 | 334.0188 | 334.0188 | 334.0188 | 337.0554 | 337.0554 | 340.0919 | 343.1285 | 343.1285 | 346.165 | 349.2015 | 349.2015 | 352.2381 | 352.2381 | 355.2746 | 358.3111 | 361.3477 | 364.3842 | 367.4207 | 370.4573 | 303.6535 | 289.1938 | 269.9142 | 257.0612 | 244.8202 | 237.9205 | 231.1227 | 228.7489 | 219.9114 | 209.4394 | 203.1944 | 195.2939 | 185.9942 | 177.1373 | 170.2359 | 162.1294 | 155.8 | 149.7058 | 142.577 | 136.9892 | 131.6104 | 125.3432 | 120.4125 | 114.6786 | 110.1593 | 105.8103 | 101.6257 | 97.5997 | 93.7267 | 90.0012
|  | Both | Sewered | Building | AeMBR | Graywater | Labor | Maintenance Labor | Chlorination | Maintenance Labor | 596.5348 | $/yr | Annual |  |  |  | 9628.7119 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 596.5348 | 568.1284 | 541.0746 | 515.3092 | 490.7706 | 467.4006 | 445.1434 | 423.9461 | 403.7582 | 384.5316 | 366.2206 | 348.7815 | 332.1729 | 316.3551 | 301.2906 | 286.9434 | 273.2795 | 260.2662 | 247.8725 | 236.0691 | 224.8277 | 214.1216 | 203.9253 | 194.2146 | 184.9663 | 176.1584 | 167.7699 | 159.7808 | 152.1722 | 144.9259
|  | Both | Sewered | Building | AeMBR | Mixed WW | Labor | Maintenance Labor | Chlorination | Maintenance Labor | 712.0003 | $/yr | Annual |  |  |  | 11492.4494 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 712.0003 | 678.0955 | 645.8053 | 615.0526 | 585.7644 | 557.8709 | 531.3056 | 506.0053 | 481.9098 | 458.9617 | 437.1064 | 416.2918 | 396.4684 | 377.589 | 359.6085 | 342.4843 | 326.1755 | 310.6434 | 295.8508 | 281.7627 | 268.3454 | 255.5671 | 243.3972 | 231.8069 | 220.7684 | 210.2557 | 200.2435 | 190.7081 | 181.6267 | 172.9779
|  | Both | Sewered | Building | AnMBR | Graywater | Labor | Maintenance Labor | Chlorination | Maintenance Labor | 718.4178 | $/yr | Annual |  |  |  | 11596.0353 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 718.4178 | 684.2075 | 651.6262 | 620.5963 | 591.0441 | 562.8992 | 536.0945 | 510.5662 | 486.2535 | 463.0986 | 441.0462 | 420.044 | 400.0419 | 380.9923 | 362.8498 | 345.5713 | 329.1155 | 313.4433 | 298.5175 | 284.3023 | 270.7641 | 257.8706 | 245.591 | 233.8962 | 222.7583 | 212.1508 | 202.0484 | 192.427 | 183.2638 | 174.537
|  | Both | Sewered | Building | AnMBR | Mixed WW | Labor | Maintenance Labor | Chlorination | Maintenance Labor | 1050.6426 | $/yr | Annual |  |  |  | 16958.4996 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1050.6426 | 1000.612 | 952.9638 | 907.5846 | 864.3663 | 823.206 | 784.0057 | 746.6721 | 711.1163 | 677.2536 | 645.0034 | 614.289 | 585.0371 | 557.1782 | 530.6459 | 505.3771 | 481.3115 | 458.3919 | 436.5637 | 415.775 | 395.9761 | 377.1201 | 359.162 | 342.0591 | 325.7706 | 310.2577 | 295.4835 | 281.4129 | 268.0122 | 255.2498
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Maintenance Labor | Chlorination | Maintenance Labor | 470.2277 | $/yr | Annual |  |  |  | 7589.9805 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 470.2277 | 447.8359 | 426.5104 | 406.2004 | 386.8575 | 368.4357 | 350.8912 | 334.1821 | 318.2686 | 303.113 | 288.679 | 274.9324 | 261.8404 | 249.3718 | 237.497 | 226.1876 | 215.4167 | 205.1588 | 195.3893 | 186.0851 | 177.2239 | 168.7847 | 160.7473 | 153.0927 | 145.8025 | 138.8596 | 132.2472 | 125.9497 | 119.9521 | 114.2401
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Maintenance Labor | Chlorination | Maintenance Labor | 549.1694 | $/yr | Annual |  |  |  | 8864.1837 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 549.1694 | 523.0185 | 498.1128 | 474.3932 | 451.803 | 430.2886 | 409.7987 | 390.2844 | 371.6995 | 353.9995 | 337.1424 | 321.088 | 305.7981 | 291.2363 | 277.3679 | 264.1599 | 251.5808 | 239.6008 | 228.1912 | 217.325 | 206.9762 | 197.1202 | 187.7335 | 178.7938 | 170.2798 | 162.1712 | 154.4488 | 147.0941 | 140.0896 | 133.4187
|  | Both | Sewered | District | AeMBR | Graywater | Labor | Maintenance Labor | Chlorination | Maintenance Labor | 736.1975 | $/yr | Annual |  |  |  | 11883.0178 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 736.1975 | 701.1405 | 667.7528 | 635.9551 | 605.6715 | 576.83 | 549.3619 | 523.2018 | 498.2874 | 474.5595 | 451.9614 | 430.4394 | 409.9423 | 390.4212 | 371.8298 | 354.1236 | 337.2605 | 321.2005 | 305.9053 | 291.3383 | 277.4651 | 264.2525 | 251.669 | 239.6848 | 228.2712 | 217.4012 | 207.0487 | 197.1893 | 187.7993 | 178.8565
|  | Both | Both | District | AeMBR | Mixed WW | Labor | Maintenance Labor | Chlorination | Maintenance Labor | 888.9625 | $/yr | Annual |  |  |  | 14348.8087 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 888.9625 | 846.6309 | 806.3152 | 767.9192 | 731.3516 | 696.5254 | 663.3575 | 631.769 | 601.6848 | 573.0331 | 545.7458 | 519.7579 | 495.0076 | 471.4358 | 448.9865 | 427.6062 | 407.244 | 387.8514 | 369.3823 | 351.7926 | 335.0406 | 319.0863 | 303.8917 | 289.4207 | 275.6387 | 262.5131 | 250.0125 | 238.1071 | 226.7687 | 215.9702
|  | Both | Both | Both | All | Mixed WW | Capital | Capital | Chlorination | Contact Basin, Direct and Indirect Cost | 3996 | $ | Year 1 |  |  | Direct and Indirect Cost | 3996 | 3996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Equalization | Aerators, Direct + Indirect | 48096 | $ | Year 1 |  |  | Direct and Indirect Cost | 48096 | 48096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Equalization | Tank, Direct + Indirect | 23019 | $ | Year 1 |  |  | Direct and Indirect Cost | 23019 | 23019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Equalization | Aerators, Direct + Indirect | 45499 | $ | Year 1 |  |  | Direct and Indirect Cost | 45499 | 45499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Equalization | Tank, Direct + Indirect | 17771 | $ | Year 1 |  |  | Direct and Indirect Cost | 17771 | 17771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Capital | Capital | Equalization | Aerators, Direct + Indirect | 42132 | $ | Year 1 |  |  | Direct and Indirect Cost | 42132 | 42132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Capital | Capital | Equalization | Tank, Direct + Indirect | 17997 | $ | Year 1 |  |  | Direct and Indirect Cost | 17997 | 17997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | Equalization | Aerators, Direct + Indirect | 48096 | $ | Year 1 |  |  | Direct and Indirect Cost | 48096 | 48096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | Equalization | Tank, Direct + Indirect | 31566 | $ | Year 1 |  |  | Direct and Indirect Cost | 31566 | 31566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Capital | Capital | Equalization | Aerators, Direct + Indirect | 39428 | $ | Year 1 |  |  | Direct and Indirect Cost | 39428 | 39428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Capital | Capital | Equalization | Tank, Direct + Indirect | 13712 | $ | Year 1 |  |  | Direct and Indirect Cost | 13712 | 13712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | Equalization | Aerators, Direct + Indirect | 43742 | $ | Year 1 |  |  | Direct and Indirect Cost | 43742 | 43742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | Equalization | Tank, Direct + Indirect | 23775 | $ | Year 1 |  |  | Direct and Indirect Cost | 23775 | 23775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | General | Zeolite | Maintenance materials | 989.9619 | $/yr | Annual |  |  |  | 15979.0481 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 942.8209 | 897.9246 | 855.1663 | 814.4441 | 775.6611 | 738.7248 | 703.5474 | 670.0452 | 638.1383 | 607.7507 | 578.8102 | 551.2478 | 524.9979 | 499.998 | 476.1886 | 453.513 | 431.9171 | 411.3496 | 391.7615 | 373.1062 | 355.3393 | 338.4184 | 322.3032 | 306.9554 | 292.3385 | 278.4176 | 265.1596 | 252.533 | 240.5076
|  | Both | Sewered | Building | All MBR | Mixed WW | Capital | Capital | Fine Screen | Fine Screen, Direct + Indirect | 37812 | $ | Year 1 |  |  | Direct and Indirect Cost | 37812 | 37812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Capital | Capital | Fine Screen | Fine Screen, Direct + Indirect | 28630 | $ | Year 1 |  |  | Direct and Indirect Cost | 28630 | 28630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | All MBR | Mixed WW | Capital | Capital | Fine Screen | Fine Screen, Direct + Indirect | 58245 | $ | Year 1 |  |  | Direct and Indirect Cost | 58245 | 58245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | All MBR | Graywater | Capital | Capital | Fine Screen | Fine Screen, Direct + Indirect | 43237 | $ | Year 1 |  |  | Direct and Indirect Cost | 43237 | 43237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | All | All | Both | Capital | Capital | Chlorination | Chlorine Pumps and Injector, Direct + Indirect | 55075 | $ | Year 1 |  |  | Direct and Indirect Cost | 55075 | 55075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All | Graywater | Capital | Capital | Chlorination | Contact Basin, Direct and Indirect Cost | 2943 | $ | Year 1 |  |  | Direct and Indirect Cost | 2943 | 2943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | UV | UV System, Direct and Indirect | 4958 | $ | Year 1 |  |  | Direct and Indirect Cost | 4958 | 4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | AeMBR | Sludge Pump | 2349 | $ | Year 1 | 25 | CAPDET, Pumps | Equipment + Installation | 2349 | 2349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All | Mixed WW | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage, Direct +Indirect | 14274 | $ | Year 1 |  |  | Direct and Indirect Cost | 14274 | 14274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage, Direct +Indirect | 9516 | $ | Year 1 |  |  | Direct and Indirect Cost | 9516 | 9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage, Direct +Indirect | 9516 | $ | Year 1 |  |  | Direct and Indirect Cost | 9516 | 9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage, Direct +Indirect | 23790 | $ | Year 1 |  |  | Direct and Indirect Cost | 23790 | 23790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | Building Reuse | Treated/Disinfected Effluent Storage, Direct +Indirect | 19032 | $ | Year 1 |  |  | Direct and Indirect Cost | 19032 | 19032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Capital | Capital | UV | UV System, Direct and Indirect | 6024 | $ | Year 1 |  |  | Direct and Indirect Cost | 6024 | 6024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Labor | Maintenance Labor | AeMBR | Maintenance Labor | 7536.3491 | $/yr | Annual |  |  |  | 121644.765 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7536.3491 | 7177.4753 | 6835.6908 | 6510.1817 | 6200.173 | 5904.9267 | 5623.7397 | 5355.9426 | 5100.8977 | 4857.9978 | 4626.6646 | 4406.3472 | 4196.5212 | 3996.6868 | 3806.3684 | 3625.1128 | 3452.4883 | 3288.0841 | 3131.5087 | 2982.3892 | 2840.3707 | 2705.115 | 2576.3 | 2453.619 | 2336.78 | 2225.5048 | 2119.5284 | 2018.5984 | 1922.4747 | 1830.9283
|  | Both | Sewered | Building | AeMBR | Graywater | Labor | Maintenance Labor | AeMBR | Maintenance Labor | 5127.9011 | $/yr | Annual |  |  |  | 82769.8296 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 5127.9011 | 4883.7154 | 4651.1575 | 4429.6738 | 4218.737 | 4017.8447 | 3826.5188 | 3644.3036 | 3470.7653 | 3305.4908 | 3148.0865 | 2998.1776 | 2855.4072 | 2719.4355 | 2589.9385 | 2466.6081 | 2349.1506 | 2237.2863 | 2130.7488 | 2029.2846 | 1932.652 | 1840.621 | 1752.9723 | 1669.4975 | 1589.9976 | 1514.2834 | 1442.1747 | 1373.4997 | 1308.095 | 1245.8047
|  | Both | Sewered | Building | AeMBR | Mixed WW | Labor | Operations Labor | AeMBR | Operations Labor | 17280.2217 | $/yr | Annual |  |  |  | 278921.3299 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 17280.2217 | 16457.354 | 15673.6705 | 14927.3052 | 14216.4812 | 13539.5059 | 12894.7675 | 12280.7309 | 11695.9342 | 11138.985 | 10608.5571 | 10103.3877 | 9622.274 | 9164.0705 | 8727.6862 | 8312.0821 | 7916.2687 | 7539.3035 | 7180.289 | 6838.3705 | 6512.7338 | 6202.6036 | 5907.2416 | 5625.9443 | 5358.0422 | 5102.8974 | 4859.9023 | 4628.4783 | 4408.0746 | 4198.1663
|  | Both | Sewered | Building | AeMBR | Graywater | Labor | Operations Labor | AeMBR | Operations Labor | 12186.2505 | $/yr | Annual |  |  |  | 196699.1661 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 12186.2505 | 11605.9529 | 11053.2884 | 10526.9414 | 10025.6585 | 9548.2461 | 9093.5678 | 8660.5407 | 8248.134 | 7855.3657 | 7481.3007 | 7125.0483 | 6785.7603 | 6462.6288 | 6154.8846 | 5861.7949 | 5582.6618 | 5316.8207 | 5063.6388 | 4822.5131 | 4592.8697 | 4374.1616 | 4165.8682 | 3967.4935 | 3778.5652 | 3598.6336 | 3427.27 | 3264.0667 | 3108.635 | 2960.6047
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Fine Screen | Construction | 70633.0501 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 70633.0501 | 70633.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70633.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | Materials | Fine Screen | Maintenance | 1765.8263 | $/yr | Annual |  |  |  | 28502.3315 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1681.7393 | 1601.6565 | 1525.3871 | 1452.7496 | 1383.5711 | 1317.6867 | 1254.9398 | 1195.1807 | 1138.2673 | 1084.0641 | 1032.442 | 983.2781 | 936.4554 | 891.8623 | 849.3926 | 808.9454 | 770.4241 | 733.7373 | 698.7974 | 665.5213 | 633.8299 | 603.6475 | 574.9024 | 547.5261 | 521.4534 | 496.6223 | 472.9736 | 450.451 | 429.001
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Operations Labor | Fine Screen | Operations Labor | 13287.5855 | $/yr | Annual |  |  |  | 214475.8949 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 13287.5855 | 12654.8433 | 12052.2317 | 11478.3159 | 10931.7295 | 10411.1709 | 9915.4009 | 9443.2389 | 8993.5609 | 8565.2961 | 8157.4248 | 7768.976 | 7399.0248 | 7046.6903 | 6711.1336 | 6391.5558 | 6087.196 | 5797.3295 | 5521.2662 | 5258.3488 | 5007.9512 | 4769.4774 | 4542.3594 | 4326.0566 | 4120.0539 | 3923.8608 | 3737.0103 | 3559.0574 | 3389.5785 | 3228.17
|  | Both | Sewered | Building | RVFW | Mixed WW | Energy | Electricity | Fine Screen | Electricity | 561.5798 | $/yr | Annual |  |  |  | 9731.2443 | 561.5798 | 561.5798 | 550.3482 | 550.3482 | 550.3482 | 561.5798 | 572.8114 | 595.2746 | 600.8904 | 600.8904 | 612.122 | 617.7378 | 617.7378 | 617.7378 | 623.3536 | 623.3536 | 628.9694 | 634.5852 | 634.5852 | 640.201 | 645.8168 | 645.8168 | 651.4326 | 651.4326 | 657.0483 | 662.6641 | 668.2799 | 673.8957 | 679.5115 | 685.1273 | 561.5798 | 534.8379 | 499.182 | 475.4115 | 452.7728 | 440.0125 | 427.4407 | 423.0505 | 406.7063 | 387.3393 | 375.7898 | 361.1785 | 343.9795 | 327.5995 | 314.8359 | 299.8437 | 288.1381 | 276.8674 | 263.6832 | 253.3493 | 243.4015 | 231.811 | 222.6921 | 212.0877 | 203.7296 | 195.6866 | 187.9475 | 180.5018 | 173.3391 | 166.4492
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Fine Screen | Fine Screen, Direct + Indirect | 84018 | $ | Year 1 |  |  | Direct and Indirect Cost | 84018 | 84018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Fine Screen | Construction | 53481.0516 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 53481.0516 | 53481.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53481.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | Materials | Fine Screen | Maintenance | 1337.0263 | $/yr | Annual |  |  |  | 21581.0397 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1273.3584 | 1212.7223 | 1154.9736 | 1099.9748 | 1047.5951 | 997.7096 | 950.1996 | 904.952 | 861.8591 | 820.8182 | 781.7316 | 744.5063 | 709.0536 | 675.2891 | 643.1325 | 612.5071 | 583.3401 | 555.562 | 529.1067 | 503.9111 | 479.9154 | 457.0623 | 435.2974 | 414.5689 | 394.8276 | 376.0263 | 358.1202 | 341.0669 | 324.8256
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Operations Labor | Fine Screen | Operations Labor | 11426.0505 | $/yr | Annual |  |  |  | 184428.7216 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 11426.0505 | 10881.9528 | 10363.7646 | 9870.252 | 9400.24 | 8952.6095 | 8526.2948 | 8120.2808 | 7733.6007 | 7365.334 | 7014.6038 | 6680.5751 | 6362.4525 | 6059.4785 | 5770.9319 | 5496.1256 | 5234.4054 | 4985.148 | 4747.76 | 4521.6762 | 4306.3583 | 4101.2936 | 3905.9939 | 3719.9942 | 3542.8516 | 3374.1444 | 3213.4708 | 3060.4484 | 2914.7128 | 2775.9169
|  | Both | Sewered | Building | RVFW | Graywater | Energy | Electricity | Fine Screen | Electricity | 456.5863 | $/yr | Annual |  |  |  | 7911.8809 | 456.5863 | 456.5863 | 447.4545 | 447.4545 | 447.4545 | 456.5863 | 465.718 | 483.9814 | 488.5473 | 488.5473 | 497.679 | 502.2449 | 502.2449 | 502.2449 | 506.8107 | 506.8107 | 511.3766 | 515.9425 | 515.9425 | 520.5083 | 525.0742 | 525.0742 | 529.6401 | 529.6401 | 534.2059 | 538.7718 | 543.3376 | 547.9035 | 552.4694 | 557.0352 | 456.5863 | 434.8441 | 405.8544 | 386.528 | 368.1219 | 357.7473 | 347.5259 | 343.9566 | 330.668 | 314.9219 | 305.5317 | 293.6522 | 279.6687 | 266.3512 | 255.9739 | 243.7846 | 234.2675 | 225.104 | 214.3848 | 205.9828 | 197.8949 | 188.4714 | 181.0574 | 172.4356 | 165.6401 | 159.1008 | 152.8087 | 146.755 | 140.9314 | 135.3297
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Fine Screen | Fine Screen, Direct + Indirect | 63616 | $ | Year 1 |  |  | Direct and Indirect Cost | 63616 | 63616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Clarification | Slant Plate Clarifier, Direct and Indirect Installation Cost | 58903 | $ | Year 1 |  |  | Direct and Indirect Cost | 58903 | 58903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Clarification | Slant Plate Clarifier, Direct and Indirect Installation Cost | 89067 | $ | Year 1 |  |  | Direct and Indirect Cost | 89067 | 89067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Both | Capital | Capital | UV | UV System, Direct and Indirect | 12352 | $ | Year 1 |  |  | Direct and Indirect Cost | 12352 | 12352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Wetland | RVFW Effluent Storage, Direct and Indirect Cost | 14274 | $ | Year 1 |  |  | Direct and Indirect Cost | 14274 | 14274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Wetland | RVFW Effluent Storage, Direct and Indirect Cost | 9516 | $ | Year 1 |  |  | Direct and Indirect Cost | 9516 | 9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All | Mixed WW | Labor | Operations Labor | Administration | Administration Labor | 7838.2467 | $/yr | Annual |  |  |  | 126517.7166 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7838.2467 | 7464.9968 | 7109.5208 | 6770.9722 | 6448.545 | 6141.4714 | 5849.0204 | 5570.4956 | 5305.2339 | 5052.6037 | 4812.0035 | 4582.8605 | 4364.6291 | 4156.7896 | 3958.8472 | 3770.3307 | 3590.7911 | 3419.8011 | 3256.9534 | 3101.8604 | 2954.1527 | 2813.4788 | 2679.5036 | 2551.9082 | 2430.3888 | 2314.656 | 2204.4343 | 2099.4612 | 1999.4869 | 1904.2732
|  | Both | Sewered | Building | All | Graywater | Labor | Operations Labor | Administration | Administration Labor | 6182.8159 | $/yr | Annual |  |  |  | 99797.2863 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 6182.8159 | 5888.3961 | 5607.9963 | 5340.9488 | 5086.6179 | 4844.398 | 4613.7124 | 4394.0118 | 4184.7732 | 3985.4983 | 3795.7126 | 3614.9644 | 3442.8232 | 3278.8793 | 3122.7422 | 2974.0402 | 2832.4192 | 2697.5421 | 2569.0877 | 2446.7502 | 2330.2383 | 2219.2746 | 2113.5948 | 2012.9474 | 1917.0928 | 1825.8027 | 1738.8597 | 1656.0568 | 1577.197 | 1502.0924
|  | Both | Sewered | District | All | Graywater | Labor | Operations Labor | Administration | Administration Labor | 8787.8144 | $/yr | Annual |  |  |  | 141844.7593 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8787.8144 | 8369.3471 | 7970.8067 | 7591.2445 | 7229.7567 | 6885.4826 | 6557.6024 | 6245.3356 | 5947.9387 | 5664.7035 | 5394.9557 | 5138.0531 | 4893.3839 | 4660.3656 | 4438.4434 | 4227.089 | 4025.799 | 3834.0943 | 3651.5184 | 3477.6366 | 3312.0348 | 3154.3189 | 3004.1132 | 2861.0602 | 2724.8193 | 2595.066 | 2471.4914 | 2353.8013 | 2241.7155 | 2134.9672
|  | Both | Both | District | All | Mixed WW | Labor | Operations Labor | Administration | Administration Labor | 11330.3465 | $/yr | Annual |  |  |  | 182883.9569 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 11330.3465 | 10790.8062 | 10276.9583 | 9787.5793 | 9321.5041 | 8877.623 | 8454.879 | 8052.2657 | 7668.8245 | 7303.6424 | 6955.8499 | 6624.6189 | 6309.1609 | 6008.7247 | 5722.5949 | 5450.0904 | 5190.5623 | 4943.3927 | 4707.993 | 4483.8029 | 4270.2884 | 4066.9414 | 3873.2775 | 3688.8357 | 3513.1769 | 3345.8827 | 3186.555 | 3034.8143 | 2890.2993 | 2752.666
|  | Both | Sewered | Building | All | Mixed WW | Labor | Operations Labor | Administration | Lab Labor | 77057.8141 | $/yr | Annual |  |  |  | 1243795.847 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 77057.8141 | 73388.3944 | 69893.7089 | 66565.4371 | 63395.6544 | 60376.8137 | 57501.7273 | 54763.5498 | 52155.7617 | 49672.154 | 47306.8134 | 45054.108 | 42908.6742 | 40865.404 | 38919.4324 | 37066.1261 | 35301.0725 | 33620.069 | 32019.1134 | 30494.3937 | 29042.2797 | 27659.314 | 26342.2038 | 25087.8132 | 23893.1554 | 22755.3861 | 21671.7963 | 20639.806 | 19656.9581 | 18720.9124
|  | Both | Sewered | Building | All | Graywater | Labor | Operations Labor | Administration | Lab Labor | 72019.9725 | $/yr | Annual |  |  |  | 1162479.6753 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 72019.9725 | 68590.45 | 65324.2381 | 62213.5601 | 59251.0096 | 56429.533 | 53742.4123 | 51183.2499 | 48745.9522 | 46424.7164 | 44214.0156 | 42108.5863 | 40103.4155 | 38193.7291 | 36374.9801 | 34642.8382 | 32993.1792 | 31422.0754 | 29925.7861 | 28500.7487 | 27143.5702 | 25851.0192 | 24620.0183 | 23447.6365 | 22331.0824 | 21267.6975 | 20254.95 | 19290.4286 | 18371.8367 | 17496.9874
|  | Both | Sewered | District | All | Graywater | Labor | Operations Labor | Administration | Lab Labor | 79610.4485 | $/yr | Annual |  |  |  | 1284998.1065 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 79610.4485 | 75819.4747 | 72209.0236 | 68770.4986 | 65495.713 | 62376.8695 | 59406.5424 | 56577.6594 | 53883.4852 | 51317.6049 | 48873.9094 | 46546.5804 | 44330.0766 | 42219.1206 | 40208.6862 | 38293.9869 | 36470.4637 | 34733.775 | 33079.7857 | 31504.5578 | 30004.3408 | 28575.5626 | 27214.8215 | 25918.8777 | 24684.6454 | 23509.1861 | 22389.701 | 21323.5248 | 20308.1189 | 19341.0656
|  | Both | Both | District | All | Mixed WW | Labor | Operations Labor | Administration | Lab Labor | 85589.9415 | $/yr | Annual |  |  |  | 1381513.5432 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 85589.9415 | 81514.23 | 77632.6 | 73935.8095 | 70415.0567 | 67061.9587 | 63868.5321 | 60827.1735 | 57930.6414 | 55172.0394 | 52544.7995 | 50042.6661 | 47659.682 | 45390.1734 | 43228.7365 | 41170.2253 | 39209.7384 | 37342.608 | 35564.3885 | 33870.8462 | 32257.9488 | 30721.856 | 29258.9105 | 27865.629 | 26538.6943 | 25274.947 | 24071.3781 | 22925.122 | 21833.4495 | 20793.7614
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Ozone | Generator, Direct and Indirect Cost | 85678 | $ | Year 1 |  |  | Direct and Indirect Cost | 85678 | 85678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Ozone | Contact Basin | 1240 | $ | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 1240 | 1240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Chemical | Chemicals | AnMBR | Sodium Hypochlorite, membrane cleaning | 134.7865 | $/yr | Annual |  |  |  | 2175.5982 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 134.7865 | 128.3681 | 122.2553 | 116.4336 | 110.8892 | 105.6087 | 100.5797 | 95.7902 | 91.2288 | 86.8846 | 82.7472 | 78.8069 | 75.0541 | 71.4801 | 68.0763 | 64.8346 | 61.7472 | 58.8069 | 56.0066 | 53.3396 | 50.7996 | 48.3806 | 46.0767 | 43.8826 | 41.793 | 39.8028 | 37.9074 | 36.1023 | 34.3832 | 32.7459
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | AnMBR | Floating Cover | 52697 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 52697 | 52697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | AnMBR | AnMBR Minor, Direct and Indirect Install Cost | 444933 | $ | Year 1 |  |  | Direct and Indirect Cost | 444933 | 444933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 444933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Energy | Electricity | AnMBR | Operation Energy | 3501.231 | $/yr | Annual |  |  |  | 60670.5148 | 3501.231 | 3501.231 | 3431.2064 | 3431.2064 | 3431.2064 | 3501.231 | 3571.2557 | 3711.3049 | 3746.3172 | 3746.3172 | 3816.3418 | 3851.3541 | 3851.3541 | 3851.3541 | 3886.3665 | 3886.3665 | 3921.3788 | 3956.3911 | 3956.3911 | 3991.4034 | 4026.4157 | 4026.4157 | 4061.428 | 4061.428 | 4096.4403 | 4131.4526 | 4166.4649 | 4201.4773 | 4236.4896 | 4271.5019 | 3501.231 | 3334.5058 | 3112.2054 | 2964.0051 | 2822.862 | 2743.3061 | 2664.926 | 2637.5551 | 2535.655 | 2414.9095 | 2342.9028 | 2251.807 | 2144.5781 | 2042.4553 | 1962.8792 | 1869.4087 | 1796.4288 | 1726.1603 | 1643.9622 | 1579.5339 | 1517.5137 | 1445.2512 | 1388.3986 | 1322.2844 | 1270.1747 | 1220.0294 | 1171.7797 | 1125.3586 | 1080.7015 | 1037.7457
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | AnMBR | membrane | 40207.2531 | $ | Year 1 | 10 | CAPDET, membrane | Equipment + Installation | 40207.2531 | 40207.2531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40207.2531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | AnMBR | Permeate Pumps | 19440 | $ | Year 1 | 25 | CAPDET, Pumps | Equipment + Installation | 19440 | 19440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | AnMBR | Sludge Pump | 2211 | $ | Year 1 | 25 | CAPDET, Pumps | Equipment + Installation | 2211 | 2211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | AnMBR | Biogas Recirculation Blower | 18676 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 18676 | 18676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | AnMBR | Anaerobic reactor and membrane tank | 39160 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 39160 | 39160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | AnMBR | Piping (AnReactor and Membrane tank) | 23650 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 23650 | 23650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | AnMBR | Mixers | 16260 | $ | Year 1 | 15 | CAPDET, process equipment | Equipment + Installation | 16260 | 16260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Chemical | Chemicals | AnMBR | Sodium Hypochlorite, membrane cleaning | 86.2999 | $/yr | Annual |  |  |  | 1392.9735 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 86.2999 | 82.1904 | 78.2766 | 74.5491 | 70.9992 | 67.6183 | 64.3983 | 61.3317 | 58.4112 | 55.6297 | 52.9807 | 50.4578 | 48.055 | 45.7667 | 43.5873 | 41.5117 | 39.535 | 37.6524 | 35.8594 | 34.1518 | 32.5255 | 30.9767 | 29.5016 | 28.0968 | 26.7588 | 25.4846 | 24.2711 | 23.1153 | 22.0146 | 20.9663
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | AnMBR | Floating Cover | 45596 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 45596 | 45596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | AnMBR | AnMBR Minor, Direct and Indirect Install Cost | 276253 | $ | Year 1 |  |  | Direct and Indirect Cost | 276253 | 276253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | DHS | Tanks | 24790 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 24790 | 24790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | DHS | Water Distribution System | 5769 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 5769 | 5769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Labor | Operations Labor | DHS | Operation Labor | 2108.4335 | $/yr | Annual |  |  |  | 34032.3809 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2108.4335 | 2008.0319 | 1912.4114 | 1821.3442 | 1734.6135 | 1652.0129 | 1573.3456 | 1498.4244 | 1427.0708 | 1359.1151 | 1294.3953 | 1232.7574 | 1174.0547 | 1118.1473 | 1064.9022 | 1014.1926 | 965.8977 | 919.9026 | 876.0977 | 834.3787 | 794.6464 | 756.8061 | 720.7677 | 686.4455 | 653.7576 | 622.6263 | 592.9774 | 564.7404 | 537.848 | 512.2362
|  | Both | Sewered | Building | AnMBR | Mixed WW | Labor | Maintenance Labor | DHS | Maintenance Labor | 2285.0065 | $/yr | Annual |  |  |  | 36882.4588 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2285.0065 | 2176.1967 | 2072.5683 | 1973.8746 | 1879.8805 | 1790.3624 | 1705.1071 | 1623.9115 | 1546.5824 | 1472.9356 | 1402.7958 | 1335.996 | 1272.3771 | 1211.7878 | 1154.0836 | 1099.1272 | 1046.7878 | 996.9408 | 949.4674 | 904.2547 | 861.1949 | 820.1857 | 781.1292 | 743.9326 | 708.5072 | 674.7688 | 642.6369 | 612.0352 | 582.8906 | 555.1339
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | DHS | Blower | 2046 | $ | Year 1 | 15 | CAPDET, process equipment | Equipment + Installation | 2046 | 2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | DHS | Air Distribution system | 5532 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 5532 | 5532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | DHS | Sponge Media | 15378 | $ | Year 1 | 10 | CAPDET, membrane | Equipment + Installation | 15378 | 15378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | DHS | Operation and Maintenance Material Costs | 565.84 | $/yr | Annual |  |  |  | 9133.2651 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 565.84 | 538.8952 | 513.2336 | 488.7939 | 465.518 | 443.3504 | 422.2385 | 402.1319 | 382.9828 | 364.7455 | 347.3767 | 330.8349 | 315.0809 | 300.077 | 285.7877 | 272.1787 | 259.2178 | 246.8741 | 235.1182 | 223.9221 | 213.2591 | 203.1039 | 193.4323 | 184.2213 | 175.4488 | 167.0941 | 159.1373 | 151.5593 | 144.3422 | 137.4687
|  | Both | Sewered | Building | AnMBR | Mixed WW | Capital | Capital | DHS | DHS, Miscellaneous, Direct and Indirect Costs | 87092 | $ | Year 1 |  |  | Direct and Indirect Cost | 87092 | 87092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | UV | Bulbs | 70.1754 | $/replacement | Replace at Lifespan | 1 | Atlantic UV 2018 | Equipment + Installation | 1045.4826 | 0 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 70.1754 | 0 | 0 | 66.8338 | 63.6512 | 60.6202 | 57.7335 | 54.9843 | 52.366 | 49.8724 | 47.4975 | 45.2357 | 43.0816 | 41.0301 | 39.0763 | 37.2155 | 35.4434 | 33.7556 | 32.1482 | 30.6173 | 29.1593 | 27.7708 | 26.4484 | 25.1889 | 23.9895 | 22.8471 | 21.7592 | 20.723 | 19.7362 | 18.7964 | 17.9013 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | UV | Quartz Sleeve | 82 | $/replacement | Replace at Lifespan | 5 | CAPDET, quartz sleeve | Equipment + Installation | 219.6109 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.4616 | 0 | 0 | 0 | 0 | 52.8579 | 0 | 0 | 0 | 0 | 41.4156 | 0 | 0 | 0 | 0 | 32.4502 | 0 | 0 | 0 | 0 | 25.4256 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | UV | UV System | 4168 | $/replacement | Replace at Lifespan | 30 | CAPDET, UV Strucutral | Equipment + Installation | 4168 | 4168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | General | UV | General Maintenance | 31.26 | $/yr | Annual |  |  |  | 504.57 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 29.7714 | 28.3537 | 27.0036 | 25.7177 | 24.493 | 23.3267 | 22.2159 | 21.158 | 20.1505 | 19.1909 | 18.2771 | 17.4067 | 16.5778 | 15.7884 | 15.0366 | 14.3206 | 13.6386 | 12.9892 | 12.3706 | 11.7816 | 11.2205 | 10.6862 | 10.1774 | 9.6927 | 9.2312 | 8.7916 | 8.3729 | 7.9742 | 7.5945
|  | Both | Sewered | Building | AnMBR | Graywater | Energy | Electricity | UV | Operational Electricity | 74.774 | $/yr | Annual |  |  |  | 1295.709 | 74.774 | 74.774 | 73.2785 | 73.2785 | 73.2785 | 74.774 | 76.2695 | 79.2604 | 80.0082 | 80.0082 | 81.5036 | 82.2514 | 82.2514 | 82.2514 | 82.9991 | 82.9991 | 83.7469 | 84.4946 | 84.4946 | 85.2423 | 85.9901 | 85.9901 | 86.7378 | 86.7378 | 87.4856 | 88.2333 | 88.981 | 89.7288 | 90.4765 | 91.2243 | 74.774 | 71.2133 | 66.4658 | 63.3007 | 60.2864 | 58.5874 | 56.9135 | 56.3289 | 54.1527 | 51.574 | 50.0362 | 48.0907 | 45.8007 | 43.6197 | 41.9202 | 39.924 | 38.3654 | 36.8647 | 35.1093 | 33.7333 | 32.4088 | 30.8655 | 29.6513 | 28.2393 | 27.1265 | 26.0555 | 25.0251 | 24.0337 | 23.08 | 22.1626
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | UV | UV System, Direct and Indirect | 4958 | $ | Year 1 |  |  | Direct and Indirect Cost | 4958 | 4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | DHS | Tanks | 19398 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 19398 | 19398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | DHS | Water Distribution System | 3647 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 3647 | 3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Labor | Operations Labor | DHS | Operation Labor | 1843.4021 | $/yr | Annual |  |  |  | 29754.4897 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1843.4021 | 1755.6211 | 1672.0201 | 1592.4001 | 1516.5715 | 1444.3538 | 1375.5751 | 1310.0715 | 1247.6871 | 1188.2735 | 1131.689 | 1077.7991 | 1026.4753 | 977.5955 | 931.0433 | 886.708 | 844.4838 | 804.2703 | 765.9717 | 729.4968 | 694.7589 | 661.6751 | 630.1668 | 600.1588 | 571.5799 | 544.3618 | 518.4398 | 493.7522 | 470.2402 | 447.8478
|  | Both | Sewered | Building | AnMBR | Graywater | Labor | Maintenance Labor | DHS | Maintenance Labor | 2050.1667 | $/yr | Annual |  |  |  | 33091.8921 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 2050.1667 | 1952.5397 | 1859.5617 | 1771.0111 | 1686.6772 | 1606.3593 | 1529.866 | 1457.0152 | 1387.6335 | 1321.5558 | 1258.6245 | 1198.69 | 1141.6096 | 1087.2472 | 1035.4735 | 986.1653 | 939.205 | 894.481 | 851.8866 | 811.3206 | 772.6863 | 735.8917 | 700.8492 | 667.4755 | 635.6909 | 605.4199 | 576.5904 | 549.1337 | 522.9845 | 498.0805
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | DHS | Blower | 1553 | $ | Year 1 | 15 | CAPDET, process equipment | Equipment + Installation | 1553 | 1553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | DHS | Air Distribution system | 3409 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 3409 | 3409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | DHS | Sponge Media | 9842 | $ | Year 1 | 10 | CAPDET, membrane | Equipment + Installation | 9842 | 9842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | DHS | Operation and Maintenance Material Costs | 401.785 | $/yr | Annual |  |  |  | 6485.2412 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 401.785 | 382.6524 | 364.4308 | 347.077 | 330.5495 | 314.8091 | 299.8182 | 285.5411 | 271.9439 | 258.9942 | 246.6611 | 234.9154 | 223.7289 | 213.0752 | 202.9287 | 193.2655 | 184.0623 | 175.2975 | 166.95 | 159 | 151.4285 | 144.2177 | 137.3502 | 130.8097 | 124.5806 | 118.6482 | 112.9983 | 107.6174 | 102.4928 | 97.6122
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | DHS | DHS, Miscellaneous, Direct and Indirect Costs | 46776 | $ | Year 1 |  |  | Direct and Indirect Cost | 46776 | 46776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | Zeolite | Adsorption Vessel - Steel | 46495.2608 | $/replacement | Replace at Lifespan | 40 | CAPDET, Structural | Equipment + Installation | 46495.2608 | 46495.2608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46495.2608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | Zeolite | Feed System (pumps and piping | 11760.8567 | $ | Year 1 | 25 | CAPDET, pumps | Equipment + Installation | 11760.8567 | 11760.8567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11760.8567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | Zeolite | Regeneration System | 16259.9569 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 16259.9569 | 16259.9569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16259.9569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | Zeolite | Zeolite Replacement System | 24386.4332 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 24386.4332 | 24386.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24386.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Capital | Capital | Zeolite | Misc., Direct, and Indirect Install Cost | 141866 | $ | Year 1 |  |  | Direct and Indirect Cost | 141866 | 141866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Chemical | Materials | Zeolite | Zeolite | 684.7217 | $/yr | Annual |  |  |  | 11052.1427 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 684.7217 | 652.1159 | 621.0627 | 591.4883 | 563.3222 | 536.4973 | 510.9498 | 486.6189 | 463.4466 | 441.3777 | 420.3597 | 400.3426 | 381.2786 | 363.1225 | 345.831 | 329.3628 | 313.6789 | 298.7418 | 284.516 | 270.9676 | 258.0644 | 245.7756 | 234.072 | 222.9257 | 212.3102 | 202.2002 | 192.5716 | 183.4015 | 174.6681 | 166.3506
|  | Both | Sewered | Building | AnMBR | Graywater | Chemical | Chemicals | Zeolite | NaCl | 48.7985 | $/yr | Annual |  |  |  | 787.6609 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 48.7985 | 46.4748 | 44.2617 | 42.154 | 40.1467 | 38.2349 | 36.4142 | 34.6802 | 33.0288 | 31.456 | 29.9581 | 28.5315 | 27.1729 | 25.8789 | 24.6466 | 23.4729 | 22.3552 | 21.2906 | 20.2768 | 19.3112 | 18.3917 | 17.5159 | 16.6818 | 15.8874 | 15.1309 | 14.4103 | 13.7241 | 13.0706 | 12.4482 | 11.8554
|  | Both | Sewered | Building | AnMBR | Graywater | Chemical | Chemicals | Zeolite | NaOH | 1327.3168 | $/yr | Annual |  |  |  | 21424.3179 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1327.3168 | 1264.1112 | 1203.9155 | 1146.5861 | 1091.9868 | 1039.9874 | 990.4642 | 943.2993 | 898.3802 | 855.6002 | 814.8574 | 776.0546 | 739.0997 | 703.9044 | 670.3852 | 638.4621 | 608.0591 | 579.1039 | 551.5275 | 525.2643 | 500.2517 | 476.4302 | 453.7431 | 432.1363 | 411.5583 | 391.9603 | 373.2955 | 355.5196 | 338.5901 | 322.4667
|  | Both | Sewered | Building | AnMBR | Graywater | Energy | Electricity | Zeolite | Electricity | 144.1365 | $/yr | Annual |  |  |  | 2497.6467 | 144.1365 | 144.1365 | 141.2538 | 141.2538 | 141.2538 | 144.1365 | 147.0193 | 152.7847 | 154.2261 | 154.2261 | 157.1088 | 158.5502 | 158.5502 | 158.5502 | 159.9916 | 159.9916 | 161.4329 | 162.8743 | 162.8743 | 164.3157 | 165.757 | 165.757 | 167.1984 | 167.1984 | 168.6398 | 170.0811 | 171.5225 | 172.9638 | 174.4052 | 175.8466 | 144.1365 | 137.2729 | 128.1214 | 122.0204 | 116.2099 | 112.9348 | 109.708 | 108.5813 | 104.3863 | 99.4155 | 96.4512 | 92.701 | 88.2867 | 84.0826 | 80.8066 | 76.9587 | 73.9543 | 71.0615 | 67.6776 | 65.0253 | 62.4721 | 59.4972 | 57.1567 | 54.435 | 52.2898 | 50.2254 | 48.2391 | 46.3281 | 44.4897 | 42.7213
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | General | Zeolite | Maintenance materials | 1723.3409 | $/yr | Annual |  |  |  | 27816.5726 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1723.3409 | 1641.2771 | 1563.121 | 1488.6867 | 1417.7968 | 1350.2827 | 1285.9835 | 1224.7462 | 1166.425 | 1110.8809 | 1057.9818 | 1007.6017 | 959.6207 | 913.9245 | 870.4043 | 828.9564 | 789.4823 | 751.8879 | 716.0837 | 681.9845 | 649.5091 | 618.5801 | 589.1239 | 561.0704 | 534.3527 | 508.9073 | 484.6737 | 461.594 | 439.6133 | 418.6793
|  | Both | Sewered | District | AeMBR | Graywater | Labor | Operations Labor | Chlorination | Operations Labor | 1792.4049 | $/yr | Annual |  |  |  | 28931.3396 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1792.4049 | 1707.0523 | 1625.7641 | 1548.3468 | 1474.616 | 1404.3962 | 1337.5201 | 1273.8287 | 1213.1702 | 1155.4002 | 1100.3811 | 1047.982 | 998.0781 | 950.5506 | 905.2863 | 862.1774 | 821.1213 | 782.0203 | 744.7813 | 709.3155 | 675.5386 | 643.3701 | 612.7334 | 583.5556 | 555.7672 | 529.3021 | 504.0973 | 480.0926 | 457.2311 | 435.4582
|  | Both | Both | District | AeMBR | Mixed WW | Labor | Operations Labor | Chlorination | Operations Labor | 2466.2081 | $/yr | Annual |  |  |  | 39807.2458 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2466.2081 | 2348.7696 | 2236.9234 | 2130.4032 | 2028.9555 | 1932.3385 | 1840.3224 | 1752.688 | 1669.2267 | 1589.7397 | 1514.0378 | 1441.9408 | 1373.2769 | 1307.8828 | 1245.6027 | 1186.2882 | 1129.7983 | 1075.9984 | 1024.7604 | 975.9623 | 929.4879 | 885.2266 | 843.0729 | 802.9266 | 764.692 | 728.2781 | 693.5982 | 660.5697 | 629.114 | 599.1562
|  | Both | Both | District | AeMBR | Both | Capital | Capital | UV | UV System, Direct and Indirect | 12352 | $ | Year 1 |  |  | Direct and Indirect Cost | 12352 | 12352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Sludge Pump | 4860 | $ | Year 1 | 25 | CAPDET, pumps | Equipment + Installation | 4860 | 4860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Capital | Capital | AeMBR | Sludge Pump | 3143 | $ | Year 1 | 25 | CAPDET, pumps | Equipment + Installation | 3143 | 3143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Labor | Maintenance Labor | AeMBR | Maintenance Labor | 9237.9247 | $/yr | Annual |  |  |  | 149110.0227 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 9237.9247 | 8798.0235 | 8379.07 | 7980.0667 | 7600.0635 | 7238.1557 | 6893.4817 | 6565.2206 | 6252.5911 | 5954.8486 | 5671.2844 | 5401.2233 | 5144.0222 | 4899.0687 | 4665.7797 | 4443.5997 | 4231.9998 | 4030.476 | 3838.5485 | 3655.7605 | 3481.6767 | 3315.8825 | 3157.9834 | 3007.6032 | 2864.384 | 2727.9848 | 2598.0807 | 2474.3626 | 2356.5358 | 2244.3198
|  | Both | Sewered | District | AeMBR | Graywater | Labor | Maintenance Labor | AeMBR | Maintenance Labor | 6727.3526 | $/yr | Annual |  |  |  | 108586.694 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6727.3526 | 6407.0025 | 6101.9072 | 5811.3402 | 5534.6097 | 5271.0568 | 5020.0541 | 4781.0039 | 4553.3371 | 4336.5115 | 4130.0109 | 3933.3438 | 3746.0417 | 3567.6587 | 3397.7702 | 3235.9716 | 3081.8778 | 2935.1217 | 2795.354 | 2662.2419 | 2535.4685 | 2414.7319 | 2299.7446 | 2190.233 | 2085.9362 | 1986.6059 | 1892.0056 | 1801.9101 | 1716.1049 | 1634.3856
|  | Both | Both | District | AeMBR | Mixed WW | Labor | Operations Labor | AeMBR | Operations Labor | 20784.7719 | $/yr | Annual |  |  |  | 335488.5319 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 20784.7719 | 19795.0208 | 18852.4008 | 17954.6674 | 17099.6832 | 16285.4126 | 15509.9168 | 14771.3493 | 14067.9517 | 13398.0493 | 12760.0469 | 12152.4256 | 11573.7387 | 11022.6083 | 10497.7222 | 9997.8306 | 9521.7435 | 9068.3271 | 8636.502 | 8225.24 | 7833.5619 | 7460.5352 | 7105.2716 | 6766.9253 | 6444.6908 | 6137.8007 | 5845.5245 | 5567.1662 | 5302.0631 | 5049.5839
|  | Both | Sewered | District | AeMBR | Graywater | Labor | Operations Labor | AeMBR | Operations Labor | 15588.9254 | $/yr | Annual |  |  |  | 251621.9919 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 15588.9254 | 14846.5956 | 14139.6149 | 13466.2999 | 12825.0475 | 12214.331 | 11632.6962 | 11078.7582 | 10551.1983 | 10048.7603 | 9570.2479 | 9114.5218 | 8680.497 | 8267.14 | 7873.4666 | 7498.5397 | 7141.4663 | 6801.3965 | 6477.5205 | 6169.0671 | 5875.302 | 5595.5257 | 5329.0721 | 5075.3068 | 4833.6255 | 4603.4529 | 4384.2408 | 4175.4675 | 3976.6357 | 3787.2721
|  | Both | Sewered | Building | AnMBR | Mixed WW | Labor | Maintenance Labor | AnMBR | Maintenance Labor | 7777.0176 | $/yr | Annual |  |  |  | 125529.4136 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7777.0176 | 7406.6834 | 7053.9842 | 6718.0802 | 6398.1716 | 6093.4968 | 5803.3303 | 5526.9812 | 5263.7916 | 5013.1349 | 4774.4142 | 4547.0611 | 4330.5344 | 4124.3185 | 3927.9224 | 3740.8784 | 3562.7414 | 3393.087 | 3231.5115 | 3077.63 | 2931.0761 | 2791.5011 | 2658.5725 | 2531.9738 | 2411.4036 | 2296.5749 | 2187.2142 | 2083.0611 | 1983.8677 | 1889.3978
|  | Both | Sewered | Building | AnMBR | Graywater | Labor | Maintenance Labor | AnMBR | Maintenance Labor | 6396.4542 | $/yr | Annual |  |  |  | 103245.6376 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6396.4542 | 6091.8611 | 5801.7725 | 5525.4976 | 5262.3787 | 5011.7892 | 4773.1326 | 4545.8406 | 4329.372 | 4123.2114 | 3926.868 | 3739.8743 | 3561.785 | 3392.1762 | 3230.644 | 3076.8038 | 2930.2894 | 2790.7518 | 2657.8588 | 2531.2941 | 2410.7563 | 2295.9584 | 2186.627 | 2082.5019 | 1983.3352 | 1888.8906 | 1798.9435 | 1713.2795 | 1631.6948 | 1553.995
|  | Both | Sewered | Building | AnMBR | Mixed WW | Labor | Operations Labor | AnMBR | Operations Labor | 17780.031 | $/yr | Annual |  |  |  | 286988.7882 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 17780.031 | 16933.3628 | 16127.0122 | 15359.0593 | 14627.6755 | 13931.1195 | 13267.7329 | 12635.9361 | 12034.2248 | 11461.1665 | 10915.3967 | 10395.6159 | 9900.5865 | 9429.13 | 8980.1238 | 8552.4989 | 8145.2371 | 7757.3686 | 7387.9701 | 7036.162 | 6701.1067 | 6382.0064 | 6078.1013 | 5788.6679 | 5513.017 | 5250.4924 | 5000.469 | 4762.3514 | 4535.5728 | 4319.5931
|  | Both | Sewered | Building | AnMBR | Graywater | Labor | Operations Labor | AnMBR | Operations Labor | 14891.8001 | $/yr | Annual |  |  |  | 240369.6417 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14891.8001 | 14182.6668 | 13507.3017 | 12864.0969 | 12251.5208 | 11668.1151 | 11112.4905 | 10583.3243 | 10079.3565 | 9599.3871 | 9142.2735 | 8706.9271 | 8292.3115 | 7897.4396 | 7521.371 | 7163.2105 | 6822.1052 | 6497.2431 | 6187.8505 | 5893.191 | 5612.5629 | 5345.298 | 5090.76 | 4848.3428 | 4617.4693 | 4397.5899 | 4188.1808 | 3988.7436 | 3798.8035 | 3617.9081
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Operations Labor | Equalization | Operations Labor | 2311.9658 | $/yr | Annual |  |  |  | 37317.6105 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2311.9658 | 2201.8722 | 2097.0212 | 1997.163 | 1902.06 | 1811.4857 | 1725.2245 | 1643.0709 | 1564.8295 | 1490.3138 | 1419.3465 | 1351.7585 | 1287.3891 | 1226.0848 | 1167.6998 | 1112.0951 | 1059.1382 | 1008.703 | 960.6696 | 914.9234 | 871.3556 | 829.8625 | 790.3452 | 752.7097 | 716.8664 | 682.7299 | 650.219 | 619.2562 | 589.7678 | 561.6836
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Operations Labor | Equalization | Operations Labor | 2136.6405 | $/yr | Annual |  |  |  | 34487.6722 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2136.6405 | 2034.8958 | 1937.996 | 1845.7104 | 1757.8195 | 1674.1138 | 1594.3941 | 1518.4705 | 1446.1624 | 1377.2975 | 1311.7119 | 1249.2495 | 1189.7614 | 1133.1061 | 1079.1487 | 1027.7606 | 978.8197 | 932.2092 | 887.8183 | 845.5412 | 805.2773 | 766.9308 | 730.4103 | 695.6289 | 662.5037 | 630.9559 | 600.9104 | 572.2956 | 545.0434 | 519.089
|  | Both | Sewered | Building | All MBR | Mixed WW | Labor | Operations Labor | Equalization | Operations Labor | 1997.9387 | $/yr | Annual |  |  |  | 32248.8761 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1997.9387 | 1902.7988 | 1812.1893 | 1725.8946 | 1643.7091 | 1565.4373 | 1490.8926 | 1419.8978 | 1352.2836 | 1287.8891 | 1226.5611 | 1168.1534 | 1112.527 | 1059.5496 | 1009.0948 | 961.0427 | 915.2788 | 871.6941 | 830.1848 | 790.6522 | 753.0021 | 717.1449 | 682.9951 | 650.4715 | 619.4967 | 589.9968 | 561.9018 | 535.1445 | 509.6615 | 485.3919
|  | Both | Both | District | AeMBR | Mixed WW | Labor | Operations Labor | Equalization | Operations Labor | 2419.7408 | $/yr | Annual |  |  |  | 39057.2147 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2419.7408 | 2304.5151 | 2194.7763 | 2090.2631 | 1990.7268 | 1895.9303 | 1805.6479 | 1719.6646 | 1637.7758 | 1559.7865 | 1485.511 | 1414.7723 | 1347.4022 | 1283.2402 | 1222.1335 | 1163.9367 | 1108.5112 | 1055.7249 | 1005.4523 | 957.5736 | 911.9749 | 868.5475 | 827.1881 | 787.7982 | 750.284 | 714.5562 | 680.5297 | 648.1235 | 617.2605 | 587.8671
|  | Both | Sewered | Building | All MBR | Graywater | Labor | Operations Labor | Equalization | Operations Labor | 1830.2472 | $/yr | Annual |  |  |  | 29542.1551 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1830.2472 | 1743.0926 | 1660.0882 | 1581.0364 | 1505.7489 | 1434.0466 | 1365.7587 | 1300.7225 | 1238.7834 | 1179.7937 | 1123.613 | 1070.1076 | 1019.1501 | 970.6192 | 924.3992 | 880.3802 | 838.4573 | 798.5308 | 760.5055 | 724.291 | 689.8009 | 656.9533 | 625.6698 | 595.876 | 567.5009 | 540.4771 | 514.7401 | 490.2286 | 466.8844 | 444.6518
|  | Both | Sewered | District | AeMBR | Graywater | Labor | Operations Labor | Equalization | Operations Labor | 2138.4862 | $/yr | Annual |  |  |  | 34517.4624 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2138.4862 | 2036.6535 | 1939.67 | 1847.3047 | 1759.3379 | 1675.5599 | 1595.7713 | 1519.7822 | 1447.4116 | 1378.4872 | 1312.845 | 1250.3286 | 1190.7891 | 1134.0849 | 1080.0808 | 1028.6484 | 979.6651 | 933.0144 | 888.5852 | 846.2716 | 805.9729 | 767.5933 | 731.0412 | 696.2297 | 663.0759 | 631.5009 | 601.4294 | 572.7899 | 545.5142 | 519.5373
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | AnMBR | Membrane and biogas recirculation maintance materials | 15472.8004 | $/yr | Annual |  |  |  | 249747.6101 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 15472.8004 | 14736.0004 | 14034.2861 | 13365.9868 | 12729.5112 | 12123.344 | 11546.0419 | 10996.2304 | 10472.6004 | 9973.9051 | 9498.9573 | 9046.626 | 8615.8342 | 8205.5564 | 7814.8156 | 7442.6816 | 7088.2682 | 6750.7316 | 6429.2682 | 6123.1125 | 5831.5358 | 5553.8436 | 5289.3748 | 5037.4998 | 4797.6189 | 4569.1609 | 4351.5818 | 4144.3636 | 3947.0129 | 3759.0599
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | AnMBR | Membrane and biogas recirculation maintance materials | 14235.2457 | $/yr | Annual |  |  |  | 229772.1479 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 14235.2457 | 13557.3768 | 12911.7875 | 12296.9404 | 11711.3719 | 11153.6875 | 10622.5595 | 10116.7233 | 9634.9746 | 9176.1663 | 8739.206 | 8323.0533 | 7926.7175 | 7549.2547 | 7189.7664 | 6847.3966 | 6521.3301 | 6210.7905 | 5915.0386 | 5633.3701 | 5365.1144 | 5109.6327 | 4866.3169 | 4634.5875 | 4413.8929 | 4203.7075 | 4003.531 | 3812.8866 | 3631.3206 | 3458.4006
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | AnMBR | AnMBR Mechanical Equipment Maintenance Materials | 1092.925 | $/yr | Annual |  |  | factor to reduction of maintenance is used to exclude labor costs built into the 5% factor. | 17640.9828 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1092.925 | 1040.881 | 991.3152 | 944.1097 | 899.1521 | 856.3353 | 815.5575 | 776.7214 | 739.7347 | 704.5092 | 670.9611 | 639.0106 | 608.5815 | 579.6015 | 552.0014 | 525.7156 | 500.6815 | 476.8396 | 454.1329 | 432.5075 | 411.9119 | 392.2971 | 373.6163 | 355.825 | 338.881 | 322.7438 | 307.375 | 292.7381 | 278.7982 | 265.5221
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | AnMBR | AnMBR Mechanical Equipment Maintenance Materials | 947.775 | $/yr | Annual |  |  | factor to reduction of maintenance is used to exclude labor costs built into the 5% factor. | 15298.106 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 947.775 | 902.6429 | 859.6599 | 818.7237 | 779.7368 | 742.6065 | 707.2443 | 673.566 | 641.4914 | 610.9442 | 581.8516 | 554.1444 | 527.7566 | 502.6253 | 478.6908 | 455.896 | 434.1866 | 413.5111 | 393.8201 | 375.0668 | 357.2064 | 340.1966 | 323.9968 | 308.5683 | 293.8746 | 279.8806 | 266.5529 | 253.8599 | 241.7714 | 230.2584
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Operations Labor | Clarification | Operation | 17500 | $/yr | Annual |  |  |  | 282468.7876 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 16666.6667 | 15873.0159 | 15117.158 | 14397.2933 | 13711.7079 | 13058.7694 | 12436.9233 | 11844.6888 | 11280.656 | 10743.4819 | 10231.8876 | 9744.6548 | 9280.6236 | 8838.6892 | 8417.7992 | 8016.9516 | 7635.192 | 7271.6115 | 6925.3442 | 6595.566 | 6281.4914 | 5982.3727 | 5697.4979 | 5426.1884 | 5167.7985 | 4921.7129 | 4687.3456 | 4464.1387 | 4251.5606
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Operations Labor | Clarification | Operation | 17500 | $/replacement | Annual |  |  |  | 282468.7876 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 16666.6667 | 15873.0159 | 15117.158 | 14397.2933 | 13711.7079 | 13058.7694 | 12436.9233 | 11844.6888 | 11280.656 | 10743.4819 | 10231.8876 | 9744.6548 | 9280.6236 | 8838.6892 | 8417.7992 | 8016.9516 | 7635.192 | 7271.6115 | 6925.3442 | 6595.566 | 6281.4914 | 5982.3727 | 5697.4979 | 5426.1884 | 5167.7985 | 4921.7129 | 4687.3456 | 4464.1387 | 4251.5606
|  | Both | Unsewered | District | AeMBR | Mixed WW | Energy | Electricity | AeMBR | Electricity | 7635.8579 | $/yr | Annual |  |  |  | 132316.7258 | 7635.8579 | 7635.8579 | 7483.1407 | 7483.1407 | 7483.1407 | 7635.8579 | 7788.575 | 8094.0093 | 8170.3679 | 8170.3679 | 8323.0851 | 8399.4437 | 8399.4437 | 8399.4437 | 8475.8022 | 8475.8022 | 8552.1608 | 8628.5194 | 8628.5194 | 8704.878 | 8781.2366 | 8781.2366 | 8857.5951 | 8857.5951 | 8933.9537 | 9010.3123 | 9086.6709 | 9163.0294 | 9239.388 | 9315.7466 | 7635.8579 | 7272.2456 | 6787.4292 | 6464.2183 | 6156.3984 | 5982.8944 | 5811.9546 | 5752.2613 | 5530.0266 | 5266.692 | 5109.6522 | 4910.9807 | 4677.1245 | 4454.4043 | 4280.8561 | 4077.0058 | 3917.8434 | 3764.5944 | 3585.328 | 3444.8158 | 3309.5557 | 3151.9578 | 3027.9678 | 2883.7788 | 2770.1324 | 2660.7702 | 2555.542 | 2454.302 | 2356.9091 | 2263.2264
|  | Both | Unsewered | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Diffusers | 3918 | $ | Year 1 | 10 | CADPET, fine diffuser | Equipment + Installation | 3918 | 3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Unsewered | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Swing Arms | 57678 | $ | Year 1 | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 57678 | 57678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Unsewered | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | AeMBR Process | 19225.1334 | $/yr | Annual |  |  |  | 310314.2925 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 19225.1334 | 18309.6508 | 17437.7627 | 16607.3931 | 15816.5648 | 15063.3951 | 14346.0905 | 13662.9434 | 13012.327 | 12392.6924 | 11802.5642 | 11240.5373 | 10705.2736 | 10195.4987 | 9709.9988 | 9247.6179 | 8807.2551 | 8387.862 | 7988.44 | 7608.0381 | 7245.7506 | 6900.7148 | 6572.1094 | 6259.1518 | 5961.0969 | 5677.2352 | 5406.8906 | 5149.4197 | 4904.2092 | 4670.6754
|  | Both | Unsewered | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Minor Additional Costs | 22896.2775 | $ | Year 1 |  |  | Equipment + Installation | 22896.2775 | 22896.2775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22896.2775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Unsewered | District | AeMBR | Mixed WW | Capital | Capital | AeMBR | Direct + Indirect | 299586 | $ | Year 1 |  |  | Direct and Indirect Cost | 299586 | 299586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Unsewered | District | AeMBR | Mixed WW | Chemical | Chemicals | Chlorination | Sodium Hypochlorite | 501.9424 | $/yr | Annual |  |  |  | 8101.8884 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 501.9424 | 478.0403 | 455.2765 | 433.5967 | 412.9492 | 393.285 | 374.5571 | 356.7211 | 339.7343 | 323.5565 | 308.1491 | 293.4753 | 279.5003 | 266.1907 | 253.515 | 241.4429 | 229.9456 | 218.9958 | 208.5674 | 198.6356 | 189.1768 | 180.1684 | 171.5889 | 163.418 | 155.6362 | 148.225 | 141.1666 | 134.4444 | 128.0423 | 121.945
|  | Both | Unsewered | District | AeMBR | Mixed WW | Capital | Capital | Dewatering | Equipment + Install | 66800 | $ | Year 1 | 15 | CAPDET, process Equipment | Equipment + Installation | 66800 | 66800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Unsewered | District | AeMBR | Mixed WW | Capital | Capital | Dewatering | Screw Press, Direct + Indirect | 79459 | $ | Year 1 |  |  | Direct and Indirect Cost | 79459 | 79459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Unsewered | District | AeMBR | Mixed WW | Chemical | Chemicals | Dewatering | Polymer | 344.5 | $/yr | Annual |  |  |  | 5560.5998 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 344.5 | 328.0952 | 312.4717 | 297.5921 | 283.421 | 269.9248 | 257.0712 | 244.8297 | 233.1712 | 222.0678 | 211.4931 | 201.422 | 191.8305 | 182.6957 | 173.9959 | 165.7104 | 157.8194 | 150.3042 | 143.1469 | 136.3303 | 129.8384 | 123.6556 | 117.7673 | 112.1593 | 106.8184 | 101.7318 | 96.8874 | 92.2737 | 87.8798 | 83.695
|  | Both | Unsewered | District | AeMBR | Mixed WW | Labor | Operations Labor | Dewatering | Operation Labor | 6087.5 | $/yr | Annual |  |  |  | 98258.7854 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 6087.5 | 5797.619 | 5521.542 | 5258.6114 | 5008.2013 | 4769.7155 | 4542.5862 | 4326.2726 | 4120.2596 | 3924.0568 | 3737.1969 | 3559.2352 | 3389.7478 | 3228.3312 | 3074.6012 | 2928.1916 | 2788.7539 | 2655.9561 | 2529.482 | 2409.0305 | 2294.3147 | 2185.0616 | 2081.0111 | 1981.9153 | 1887.5384 | 1797.6556 | 1712.053 | 1630.5266 | 1552.8825 | 1478.9357
|  | Both | Unsewered | District | AeMBR | Mixed WW | Materials | General | Dewatering | Material and Labor | 1670 | $/yr | Annual |  |  |  | 26955.5929 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1590.4762 | 1514.7392 | 1442.6088 | 1373.9131 | 1308.4887 | 1246.1797 | 1186.8378 | 1130.3217 | 1076.4969 | 1025.2351 | 976.4144 | 929.9185 | 885.6367 | 843.4635 | 803.2986 | 765.0462 | 728.6155 | 693.9195 | 660.8757 | 629.4054 | 599.4337 | 570.8893 | 543.7041 | 517.8134 | 493.1556 | 469.672 | 447.3067 | 426.0064 | 405.7204
|  | Both | Unsewered | District | AeMBR | Mixed WW | Materials | General | Composting | Hauling and Disposal Cost | 45208 | $/yr | Annual |  |  |  | 729705.6543 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 45208 | 43055.2381 | 41004.9887 | 39052.3702 | 37192.7335 | 35421.6509 | 33734.9057 | 32128.4816 | 30598.5539 | 29141.4799 | 27753.7904 | 26432.1813 | 25173.506 | 23974.7676 | 22833.112 | 21745.821 | 20710.3057 | 19724.1007 | 18784.8578 | 17890.3407 | 17038.4197 | 16227.0664 | 15454.349 | 14718.4276 | 14017.5501 | 13350.0477 | 12714.3311 | 12108.8868 | 11532.2731 | 10983.1173
|  | Both | Sewered | Building | AnMBR | Mixed WW | Labor | Labor | Zeolite | Operation and Maintenance Labor | 7510.9363 | $/yr | Annual |  |  |  | 121234.5757 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7510.9363 | 7153.2727 | 6812.6406 | 6488.2292 | 6179.2659 | 5885.0151 | 5604.7763 | 5337.8822 | 5083.6973 | 4841.6165 | 4611.0634 | 4391.4889 | 4182.3704 | 3983.2099 | 3793.5332 | 3612.8888 | 3440.8465 | 3276.9966 | 3120.9492 | 2972.3325 | 2830.7929 | 2695.9932 | 2567.6126 | 2445.3453 | 2328.9003 | 2218.0003 | 2112.3812 | 2011.7917 | 1915.9921 | 1824.7543
|  | Both | Sewered | Building | AnMBR | Graywater | Labor | Labor | Zeolite | Operation and Maintenance Labor | 6081.591 | $/yr | Annual |  |  |  | 98163.4073 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 6081.591 | 5791.9914 | 5516.1823 | 5253.5069 | 5003.3399 | 4765.0857 | 4538.1768 | 4322.0732 | 4116.2602 | 3920.2478 | 3733.5693 | 3555.7803 | 3386.4574 | 3225.1975 | 3071.6167 | 2925.3492 | 2786.0469 | 2653.378 | 2527.0267 | 2406.6921 | 2292.0877 | 2182.9406 | 2078.9911 | 1979.9915 | 1885.7062 | 1795.9107 | 1710.3911 | 1628.9439 | 1551.3752 | 1477.5002
|  | Both | Sewered | Building | RVFW | Mixed WW | Capital | Capital | Clarification | Sludge Pump | 3928 | $ | Year 1 | 25 | CAPDET, Pumps | Equipment + Installation | 3928 | 3928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | General | Clarification | Sludge Pump | 98.2 | $/yr | Annual |  |  |  | 1585.0534 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 93.5238 | 89.0703 | 84.8289 | 80.7894 | 76.9423 | 73.2784 | 69.7889 | 66.4656 | 63.3006 | 60.2863 | 57.4155 | 54.6814 | 52.0776 | 49.5977 | 47.2359 | 44.9866 | 42.8443 | 40.8041 | 38.8611 | 37.0105 | 35.2481 | 33.5697 | 31.9711 | 30.4487 | 28.9987 | 27.6178 | 26.3027 | 25.0502 | 23.8573
|  | Both | Sewered | Building | RVFW | Graywater | Capital | Capital | Clarification | Sludge Pump | 2219 | $ | Year 1 | 25 | CAPDET, Pumps | Equipment + Installation | 2219 | 2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | General | Clarification | Sludge Pump | 55.475 | $/yr | Annual |  |  |  | 895.4261 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 52.8333 | 50.3175 | 47.9214 | 45.6394 | 43.4661 | 41.3963 | 39.425 | 37.5477 | 35.7597 | 34.0568 | 32.4351 | 30.8906 | 29.4196 | 28.0186 | 26.6844 | 25.4137 | 24.2036 | 23.051 | 21.9533 | 20.9079 | 19.9123 | 18.9641 | 18.0611 | 17.201 | 16.3819 | 15.6018 | 14.8589 | 14.1513 | 13.4774
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | Materials | AeMBR | Pump and Blower Maintenance | 1270.15 | $/yr | Annual |  |  |  | 20501.5846 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1270.15 | 1209.6667 | 1152.0635 | 1097.2033 | 1044.9555 | 995.1958 | 947.8055 | 902.6719 | 859.6875 | 818.75 | 779.7619 | 742.6304 | 707.267 | 673.5877 | 641.5121 | 610.9639 | 581.8703 | 554.1622 | 527.7736 | 502.6415 | 478.7062 | 455.9106 | 434.2006 | 413.5244 | 393.8328 | 375.0788 | 357.2179 | 340.2075 | 324.0072 | 308.5783
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | AeMBR | Blower and Pumps | 886.725 | $/yr | Annual |  |  |  | 14312.6935 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 886.725 | 844.5 | 804.2857 | 765.9864 | 729.5109 | 694.7722 | 661.6878 | 630.1789 | 600.1704 | 571.5908 | 544.3722 | 518.4497 | 493.7617 | 470.2492 | 447.8564 | 426.5299 | 406.2189 | 386.8752 | 368.4526 | 350.9072 | 334.1973 | 318.2832 | 303.1268 | 288.6922 | 274.945 | 261.8524 | 249.3832 | 237.5078 | 226.1979 | 215.4266
|  | Both | Sewered | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Blower and Pumps | 1708 | $/yr | Annual |  |  |  | 27568.9537 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1626.6667 | 1549.2063 | 1475.4346 | 1405.1758 | 1338.2627 | 1274.5359 | 1213.8437 | 1156.0416 | 1100.992 | 1048.5638 | 998.6322 | 951.0783 | 905.7889 | 862.6561 | 821.5772 | 782.4545 | 745.1947 | 709.7093 | 675.9136 | 643.7272 | 613.0736 | 583.8796 | 556.0758 | 529.596 | 504.3771 | 480.3592 | 457.4849 | 435.6999 | 414.9523
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | AeMBR | Pumps and Blowers | 1230.1 | $/yr | Annual |  |  |  | 19855.1346 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1230.1 | 1171.5238 | 1115.737 | 1062.6066 | 1012.0063 | 963.8155 | 917.9196 | 874.2091 | 832.5801 | 792.9334 | 755.1747 | 719.214 | 684.9657 | 652.3483 | 621.2841 | 591.6991 | 563.523 | 536.6886 | 511.132 | 486.7923 | 463.6118 | 441.535 | 420.5095 | 400.4853 | 381.4145 | 363.2519 | 345.9542 | 329.4802 | 313.7907 | 298.8483
|  | Both | Unsewered | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Blowers and Pumps | 1708 | $/yr | Annual |  |  |  | 27568.9537 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1708 | 1626.6667 | 1549.2063 | 1475.4346 | 1405.1758 | 1338.2627 | 1274.5359 | 1213.8437 | 1156.0416 | 1100.992 | 1048.5638 | 998.6322 | 951.0783 | 905.7889 | 862.6561 | 821.5772 | 782.4545 | 745.1947 | 709.7093 | 675.9136 | 643.7272 | 613.0736 | 583.8796 | 556.0758 | 529.596 | 504.3771 | 480.3592 | 457.4849 | 435.6999 | 414.9523
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | General | Wetland | Pumps | 3181.925 | $/yr | Annual |  |  |  | 51359.6855 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3030.4048 | 2886.0998 | 2748.6665 | 2617.7776 | 2493.1215 | 2374.4014 | 2261.3347 | 2153.6521 | 2051.0972 | 1953.4259 | 1860.4056 | 1771.8149 | 1687.4428 | 1607.0883 | 1530.5603 | 1457.6765 | 1388.2633 | 1322.1556 | 1259.1958 | 1199.2341 | 1142.1277 | 1087.7407 | 1035.9435 | 986.6128 | 939.6313 | 894.8869 | 852.2733 | 811.6888 | 773.037
|  | Both | Sewered | Building | RVFW | Graywater | Materials | General | Wetland | Pumps | 2121.275 | $/yr | Annual |  |  |  | 34239.6559 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2020.2619 | 1924.059 | 1832.4371 | 1745.1782 | 1662.0745 | 1582.9281 | 1507.5505 | 1435.7624 | 1367.3928 | 1302.2788 | 1240.2656 | 1181.2053 | 1124.9574 | 1071.388 | 1020.3695 | 971.7805 | 925.5053 | 881.4336 | 839.4605 | 799.4862 | 761.4155 | 725.1576 | 690.6263 | 657.7393 | 626.4184 | 596.5889 | 568.1799 | 541.1238 | 515.356
|  | Low Reuse | Sewered | Building | All | Mixed WW | Capital | Capital | Building Reuse | Reuse Piping | 313402 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 313402 | 313402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Sewered | Building | All | Graywater | Capital | Capital | Building Reuse | Graywater + Reuse Piping | 626803 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 626803 | 626803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Both | District | All | Mixed WW | Capital | Capital | Building Reuse | Reuse Piping | 613421 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 613421 | 613421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Both | District | All | Graywater | Capital | Capital | Building Reuse | Graywater + Reuse Piping | 1226843 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 1226843 | 1226843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1226843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Sewered | Building | All | Mixed WW | Capital | Capital | Building Reuse | Reuse Piping | 313402 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 313402 | 313402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Sewered | Building | All | Graywater | Capital | Capital | Building Reuse | Graywater + Reuse Piping | 626803 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 626803 | 626803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Both | District | All | Mixed WW | Capital | Capital | Building Reuse | Reuse Piping | 613421 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 613421 | 613421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Both | District | All | Graywater | Capital | Capital | Building Reuse | Graywater + Reuse Piping | 1226843 | $/replacement | Replace at Lifespan | 50 | Scheuer 2003 | Equipment + Installation | 1226843 | 1226843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1226843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Sewered | Building | All | Mixed WW | Capital | Capital | Building Reuse | Installed Pump Cost | 31805.933 | $ | Year 1 | 25 | CAPDET | Equipment + Installation | 31805.933 | 31805.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31805.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Sewered | Building | All | Graywater | Capital | Capital | Building Reuse | Installed Pump Cost | 31805.933 | $ | Year 1 | 25 | CAPDET | Equipment + Installation | 31805.933 | 31805.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31805.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Both | District | All | Mixed WW | Capital | Capital | Building Reuse | Installed Pump Cost | 86367 | $ | Year 1 | 25 | CAPDET | Equipment + Installation | 86367 | 86367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Both | District | All | Graywater | Capital | Capital | Building Reuse | Installed Pump Cost | 86367 | $ | Year 1 | 25 | CAPDET | Equipment + Installation | 86367 | 86367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Sewered | Building | All | Mixed WW | Capital | Capital | Building Reuse | Installed Pump Cost | 46727.1379 | $ | Year 1 | 25 | CAPDET | Equipment + Installation | 46727.1379 | 46727.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46727.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Sewered | Building | All | Graywater | Capital | Capital | Building Reuse | Installed Pump Cost | 46412.1379 | $ | Year 1 | 25 | CAPDET | Equipment + Installation | 46412.1379 | 46412.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46412.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Both | District | All | Mixed WW | Capital | Capital | Building Reuse | Installed Pump Cost | 120517 | $ | Year 1 | 25 | CAPDET | Equipment + Installation | 120517 | 120517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Both | District | All | Graywater | Capital | Capital | Building Reuse | Installed Pump Cost | 120517 | $ | Year 1 | 25 | CAPDET | Equipment + Installation | 120517 | 120517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Sewered | Building | All | Mixed WW | Capital | Capital | Building Reuse | Ancillary Cost | 176323.7918 | $/replacement | Replace at Lifespan | 50 |  | Equipment + Installation | 176323.7918 | 176323.7918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176323.7918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Sewered | Building | All | Graywater | Capital | Capital | Building Reuse | Ancillary Cost | 333024.6171 | $/replacement | Replace at Lifespan | 50 |  | Equipment + Installation | 333024.6171 | 333024.6171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333024.6171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Both | District | All | Mixed WW | Capital | Capital | Building Reuse | Ancillary Cost | 349894.4281 | $/replacement | Replace at Lifespan | 50 |  | Equipment + Installation | 349894.4281 | 349894.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349894.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Both | District | All | Graywater | Capital | Capital | Building Reuse | Ancillary Cost | 656605.1394 | $/replacement | Replace at Lifespan | 50 |  | Equipment + Installation | 656605.1394 | 656605.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 656605.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Sewered | Building | All | Mixed WW | Capital | Capital | Building Reuse | Ancillary Cost | 183784.3942 | $/replacement | Replace at Lifespan | 50 |  | Equipment + Installation | 183784.3942 | 183784.3942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183784.3942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Sewered | Building | All | Graywater | Capital | Capital | Building Reuse | Ancillary Cost | 340327.7195 | $/replacement | Replace at Lifespan | 50 |  | Equipment + Installation | 340327.7195 | 340327.7195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340327.7195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Both | District | All | Mixed WW | Capital | Capital | Building Reuse | Ancillary Cost | 366969.3382 | $/replacement | Replace at Lifespan | 50 |  | Equipment + Installation | 366969.3382 | 366969.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366969.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Both | District | All | Graywater | Capital | Capital | Building Reuse | Ancillary Cost | 673680.0495 | $/replacement | Replace at Lifespan | 50 |  | Equipment + Installation | 673680.0495 | 673680.0495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 673680.0495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Sewered | Building | All | Mixed WW | Materials | General | Building Reuse | Pipe maintenance | 2350.515 | $/yr | Annual |  |  |  | 37939.8356 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2238.5857 | 2131.9864 | 2030.4632 | 1933.7745 | 1841.69 | 1753.9905 | 1670.4671 | 1590.9211 | 1515.1629 | 1443.0123 | 1374.2974 | 1308.8547 | 1246.5283 | 1187.1698 | 1130.6379 | 1076.798 | 1025.5219 | 976.6875 | 930.1786 | 885.8844 | 843.6994 | 803.5232 | 765.2602 | 728.8193 | 694.1136 | 661.0606 | 629.5815 | 599.6014 | 571.049
|  | Low Reuse | Sewered | Building | All | Graywater | Materials | General | Building Reuse | Pipe maintenance | 4701.0225 | $/yr | Annual |  |  |  | 75879.5501 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4477.1643 | 4263.966 | 4060.92 | 3867.5428 | 3683.3741 | 3507.9754 | 3340.9289 | 3181.8371 | 3030.321 | 2886.02 | 2748.5905 | 2617.7052 | 2493.0526 | 2374.3358 | 2261.2722 | 2153.5926 | 2051.0405 | 1953.3719 | 1860.3542 | 1771.7659 | 1687.3961 | 1607.0439 | 1530.518 | 1457.6362 | 1388.225 | 1322.119 | 1259.161 | 1199.2009 | 1142.0961
|  | Low Reuse | Both | District | All | Mixed WW | Materials | General | Building Reuse | Pipe maintenance | 4600.6575 | $/yr | Annual |  |  |  | 74259.5512 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4381.5786 | 4172.932 | 3974.2209 | 3784.9723 | 3604.7355 | 3433.0815 | 3269.6014 | 3113.9061 | 2965.6248 | 2824.4046 | 2689.9092 | 2561.8182 | 2439.8269 | 2323.6447 | 2212.9949 | 2107.6142 | 2007.2516 | 1911.6682 | 1820.6364 | 1733.9394 | 1651.3709 | 1572.7342 | 1497.8421 | 1426.5163 | 1358.5869 | 1293.8923 | 1232.2784 | 1173.5985 | 1117.7128
|  | Low Reuse | Both | District | All | Graywater | Materials | General | Building Reuse | Pipe maintenance | 9201.3225 | $/yr | Annual |  |  |  | 148519.2235 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 8763.1643 | 8345.8707 | 7948.4483 | 7569.9508 | 7209.4769 | 6866.1685 | 6539.2081 | 6227.8173 | 5931.2545 | 5648.8138 | 5379.8227 | 5123.6407 | 4879.6578 | 4647.2931 | 4425.9934 | 4215.2319 | 4014.5065 | 3823.3396 | 3641.2758 | 3467.8817 | 3302.7445 | 3145.4709 | 2995.6866 | 2853.0348 | 2717.176 | 2587.7867 | 2464.5588 | 2347.1988 | 2235.4275
|  | High Reuse | Sewered | Building | All | Mixed WW | Materials | General | Building Reuse | Pipe maintenance | 2350.515 | $/yr | Annual |  |  |  | 37939.8356 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2238.5857 | 2131.9864 | 2030.4632 | 1933.7745 | 1841.69 | 1753.9905 | 1670.4671 | 1590.9211 | 1515.1629 | 1443.0123 | 1374.2974 | 1308.8547 | 1246.5283 | 1187.1698 | 1130.6379 | 1076.798 | 1025.5219 | 976.6875 | 930.1786 | 885.8844 | 843.6994 | 803.5232 | 765.2602 | 728.8193 | 694.1136 | 661.0606 | 629.5815 | 599.6014 | 571.049
|  | High Reuse | Sewered | Building | All | Graywater | Materials | General | Building Reuse | Pipe maintenance | 4701.0225 | $/yr | Annual |  |  |  | 75879.5501 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4477.1643 | 4263.966 | 4060.92 | 3867.5428 | 3683.3741 | 3507.9754 | 3340.9289 | 3181.8371 | 3030.321 | 2886.02 | 2748.5905 | 2617.7052 | 2493.0526 | 2374.3358 | 2261.2722 | 2153.5926 | 2051.0405 | 1953.3719 | 1860.3542 | 1771.7659 | 1687.3961 | 1607.0439 | 1530.518 | 1457.6362 | 1388.225 | 1322.119 | 1259.161 | 1199.2009 | 1142.0961
|  | High Reuse | Both | District | All | Mixed WW | Materials | General | Building Reuse | Pipe maintenance | 4600.6575 | $/yr | Annual |  |  |  | 74259.5512 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4381.5786 | 4172.932 | 3974.2209 | 3784.9723 | 3604.7355 | 3433.0815 | 3269.6014 | 3113.9061 | 2965.6248 | 2824.4046 | 2689.9092 | 2561.8182 | 2439.8269 | 2323.6447 | 2212.9949 | 2107.6142 | 2007.2516 | 1911.6682 | 1820.6364 | 1733.9394 | 1651.3709 | 1572.7342 | 1497.8421 | 1426.5163 | 1358.5869 | 1293.8923 | 1232.2784 | 1173.5985 | 1117.7128
|  | High Reuse | Both | District | All | Graywater | Materials | General | Building Reuse | Pipe maintenance | 9201.3225 | $/yr | Annual |  |  |  | 148519.2235 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 8763.1643 | 8345.8707 | 7948.4483 | 7569.9508 | 7209.4769 | 6866.1685 | 6539.2081 | 6227.8173 | 5931.2545 | 5648.8138 | 5379.8227 | 5123.6407 | 4879.6578 | 4647.2931 | 4425.9934 | 4215.2319 | 4014.5065 | 3823.3396 | 3641.2758 | 3467.8817 | 3302.7445 | 3145.4709 | 2995.6866 | 2853.0348 | 2717.176 | 2587.7867 | 2464.5588 | 2347.1988 | 2235.4275
|  | Low Reuse | Sewered | Building | All | Mixed WW | Materials | General | Building Reuse | Pump Maintenance | 795.1483 | $/yr | Annual |  |  |  | 12834.5476 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 757.2841 | 721.223 | 686.879 | 654.1705 | 623.0195 | 593.3519 | 565.0971 | 538.1877 | 512.5597 | 488.1521 | 464.9068 | 442.7683 | 421.6841 | 401.6039 | 382.4799 | 364.2666 | 346.9206 | 330.4006 | 314.6672 | 299.683 | 285.4124 | 271.8214 | 258.8775 | 246.55 | 234.8095 | 223.6281 | 212.9791 | 202.8373 | 193.1784
|  | Low Reuse | Sewered | Building | All | Graywater | Materials | General | Building Reuse | Pump Maintenance | 795.1483 | $/yr | Annual |  |  |  | 12834.5476 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 757.2841 | 721.223 | 686.879 | 654.1705 | 623.0195 | 593.3519 | 565.0971 | 538.1877 | 512.5597 | 488.1521 | 464.9068 | 442.7683 | 421.6841 | 401.6039 | 382.4799 | 364.2666 | 346.9206 | 330.4006 | 314.6672 | 299.683 | 285.4124 | 271.8214 | 258.8775 | 246.55 | 234.8095 | 223.6281 | 212.9791 | 202.8373 | 193.1784
|  | Low Reuse | Both | District | All | Mixed WW | Materials | General | Building Reuse | Pump Maintenance | 2159.175 | $/yr | Annual |  |  |  | 34851.4025 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2056.3571 | 1958.4354 | 1865.1765 | 1776.3586 | 1691.7701 | 1611.2096 | 1534.4854 | 1461.4146 | 1391.8235 | 1325.5461 | 1262.4249 | 1202.3094 | 1145.0566 | 1090.5301 | 1038.6001 | 989.1429 | 942.0409 | 897.1818 | 854.4589 | 813.7703 | 775.0194 | 738.1137 | 702.9654 | 669.4909 | 637.6104 | 607.248 | 578.3314 | 550.7918 | 524.5636
|  | Low Reuse | Both | District | All | Graywater | Materials | General | Building Reuse | Pump Maintenance | 2159.175 | $/yr | Annual |  |  |  | 34851.4025 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2056.3571 | 1958.4354 | 1865.1765 | 1776.3586 | 1691.7701 | 1611.2096 | 1534.4854 | 1461.4146 | 1391.8235 | 1325.5461 | 1262.4249 | 1202.3094 | 1145.0566 | 1090.5301 | 1038.6001 | 989.1429 | 942.0409 | 897.1818 | 854.4589 | 813.7703 | 775.0194 | 738.1137 | 702.9654 | 669.4909 | 637.6104 | 607.248 | 578.3314 | 550.7918 | 524.5636
|  | High Reuse | Sewered | Building | All | Mixed WW | Materials | General | Building Reuse | Pump Maintenance | 1168.1784 | $/yr | Annual |  |  |  | 18855.6543 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1112.5509 | 1059.5723 | 1009.1165 | 961.0633 | 915.2984 | 871.7127 | 830.2026 | 790.6692 | 753.0182 | 717.1602 | 683.0097 | 650.4855 | 619.51 | 590.0095 | 561.9138 | 535.156 | 509.6724 | 485.4023 | 462.2879 | 440.2742 | 419.3087 | 399.3417 | 380.3254 | 362.2146 | 344.9663 | 328.5394 | 312.8946 | 297.9949 | 283.8047
|  | High Reuse | Sewered | Building | All | Graywater | Materials | General | Building Reuse | Pump Maintenance | 1160.3034 | $/yr | Annual |  |  |  | 18728.5433 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1105.0509 | 1052.4294 | 1002.3137 | 954.5845 | 909.1281 | 865.8363 | 824.606 | 785.339 | 747.9419 | 712.3257 | 678.4054 | 646.1004 | 615.3337 | 586.0321 | 558.1258 | 531.5484 | 506.2366 | 482.13 | 459.1715 | 437.3062 | 416.4821 | 396.6496 | 377.7615 | 359.7729 | 342.6408 | 326.3246 | 310.7853 | 295.986 | 281.8915
|  | High Reuse | Both | District | All | Mixed WW | Materials | General | Building Reuse | Pump Maintenance | 3012.925 | $/yr | Annual |  |  |  | 48631.8441 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 2869.4524 | 2732.8118 | 2602.6779 | 2478.7409 | 2360.7056 | 2248.291 | 2141.2295 | 2039.2662 | 1942.1583 | 1849.6746 | 1761.5948 | 1677.7094 | 1597.8185 | 1521.7319 | 1449.2684 | 1380.2557 | 1314.5292 | 1251.9326 | 1192.3167 | 1135.5397 | 1081.4664 | 1029.968 | 980.9219 | 934.2114 | 889.7251 | 847.3572 | 807.0069 | 768.578 | 731.979
|  | High Reuse | Both | District | All | Graywater | Materials | General | Building Reuse | Pump Maintenance | 3012.925 | $/yr | Annual |  |  |  | 48631.8441 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 2869.4524 | 2732.8118 | 2602.6779 | 2478.7409 | 2360.7056 | 2248.291 | 2141.2295 | 2039.2662 | 1942.1583 | 1849.6746 | 1761.5948 | 1677.7094 | 1597.8185 | 1521.7319 | 1449.2684 | 1380.2557 | 1314.5292 | 1251.9326 | 1192.3167 | 1135.5397 | 1081.4664 | 1029.968 | 980.9219 | 934.2114 | 889.7251 | 847.3572 | 807.0069 | 768.578 | 731.979
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | Thermal Recovery | Heat Pump | 43765.0345 | $ | Year 1 | 15 | CAPDET, mechanical equipment | Equipment + Installation | 43765.0345 | 43765.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43765.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | Thermal Recovery | Heat Pump | 34485.6574 | $ | Year 1 | 15 | CAPDET, mechanical equipment | Equipment + Installation | 34485.6574 | 34485.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34485.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | General | Thermal Recovery | Heat Pump Maintenance | 1094.1259 | $/yr | Annual |  |  |  | 17660.3661 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1042.0246 | 992.4044 | 945.1471 | 900.1401 | 857.2762 | 816.4536 | 777.5748 | 740.5475 | 705.2833 | 671.6984 | 639.7127 | 609.2502 | 580.2383 | 552.6079 | 526.2932 | 501.2317 | 477.3635 | 454.6319 | 432.9828 | 412.3645 | 392.7281 | 374.0268 | 356.216 | 339.2533 | 323.0984 | 307.7128 | 293.0598 | 279.1045 | 265.8139
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | General | Thermal Recovery | Heat Pump Maintenance | 862.1414 | $/yr | Annual |  |  |  | 13915.8883 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 821.0871 | 781.9877 | 744.7502 | 709.2859 | 675.5104 | 643.3432 | 612.7078 | 583.5313 | 555.7441 | 529.2801 | 504.0762 | 480.0726 | 457.212 | 435.44 | 414.7048 | 394.9569 | 376.1495 | 358.2376 | 341.1786 | 324.932 | 309.4591 | 294.7229 | 280.6885 | 267.3224 | 254.5928 | 242.4693 | 230.9231 | 219.9268 | 209.4541
|  | Both | Sewered | Building | AeMBR | Mixed WW | Capital | Capital | Thermal Recovery | Direct + Indirect | 52058.5086 | $ | Year 1 |  |  | Direct and Indirect Cost | 52058.5086 | 52058.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52058.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Capital | Capital | Thermal Recovery | Direct + Indirect | 41020.6895 | $ | Year 1 |  |  | Direct and Indirect Cost | 41020.6895 | 41020.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41020.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | Materials | Ozone | Generator + Ancillary Equipment | 72029 | $/replacement | Replace at Lifespan | 10 | Eagleton 1999 | Equipment + Installation | 74934.8568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46430.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28504.3212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | Materials | Wetland | Gravel | 3536 | $/replacement | Replace at Lifespan | 10 |  | Equipment + Installation | 3678.6524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2279.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1399.3153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | Materials | Wetland | Wood Chips | 857 | $/replacement | Replace at Lifespan | 2 | RSMeans | Equipment + Installation | 6539.5511 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 857 | 0 | 0 | 0 | 816.1905 | 0 | 740.3088 | 0 | 671.4819 | 0 | 609.0539 | 0 | 552.4298 | 0 | 501.0702 | 0 | 454.4854 | 0 | 412.2317 | 0 | 373.9063 | 0 | 339.144 | 0 | 307.6136 | 0 | 279.0146 | 0 | 253.0745 | 0 | 229.546 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | Materials | Wetland | Pumps | 127277 | $/replacement | Replace at Lifespan | 25 | RSMeans for cost, Lifespan CAPDET | Equipment + Installation | 39464.5134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39464.5134 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | Materials | Wetland | Crushed Limestone | 1375 | $/replacement | Replace at Lifespan | 10 |  | Equipment + Installation | 1430.4715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 886.3373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | All | All | Both | Materials | Materials | Chlorination | Chlorine Pumps and Injector | 46300.9901 | $/replacement | Replace at Lifespan | 25 | CAPDET, Pumps | Equipment + Installation | 14356.4512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46300.9901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14356.4512 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | Materials | Wetland | Gravel | 2357 | $/replacement | Replace at Lifespan | 10 |  | Equipment + Installation | 2452.0882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1519.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 932.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | Materials | Wetland | Wood Chips | 571 | $/replacement | Replace at Lifespan | 2 | RSMeans | Equipment + Installation | 4357.1572 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 571 | 0 | 0 | 0 | 543.8095 | 0 | 493.2513 | 0 | 447.3934 | 0 | 405.799 | 0 | 368.0717 | 0 | 333.8519 | 0 | 302.8135 | 0 | 274.6608 | 0 | 249.1254 | 0 | 225.9641 | 0 | 204.9561 | 0 | 185.9012 | 0 | 168.6179 | 0 | 152.9414 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | Materials | Wetland | Pumps | 84851 | $/replacement | Replace at Lifespan | 25 | RSMeans for cost, Lifespan CAPDET | Equipment + Installation | 26309.5723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26309.5723 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | Materials | Wetland | Crushed Limestone | 917 | $/replacement | Replace at Lifespan | 10 |  | Equipment + Installation | 953.9944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591.1064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | Materials | Equalization | Aerators | 40433.7165 | $/replacement | Replace at Lifespan | 15 | CAPDET, Aerators | Equipment + Installation | 20421.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40433.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20421.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | Materials | Equalization | Aerators | 38250.5109 | $/replacement | Replace at Lifespan | 15 | CAPDET, Aerators | Equipment + Installation | 19319.1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38250.5109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19319.1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Materials | Materials | Fine Screen | Construction | 31788.103 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 16055.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31788.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16055.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Materials | Materials | Fine Screen | Construction | 24068.9192 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 12156.4398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24068.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12156.4398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Mixed WW | Materials | Materials | Equalization | Aerators | 35419.7746 | $/replacement | Replace at Lifespan | 15 | CAPDET, Aerators | Equipment + Installation | 17889.3931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35419.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17889.3931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | Materials | AeMBR | Blowers | 23530 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 11884.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11884.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | Materials | AeMBR | Membrane | 23559 | $/replacement | Replace at Lifespan | 10 | CAPDET, membrane | Equipment + Installation | 24509.4378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15186.3415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9323.0963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | Materials | AeMBR | Permeate Pumps | 23670 | $/replacement | Replace at Lifespan | 25 | CAPDET, pumps | Equipment + Installation | 7339.3074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7339.3074 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | Materials | AeMBR | Swing Arms | 48669.2015 | $/replacement | Replace at Lifespan | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 19260.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48669.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19260.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | Materials | AeMBR | Diffusers | 2141 | $/replacement | Replace at Lifespan | 10 | CADPET, fine diffuser | Equipment + Installation | 2227.3741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1380.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 847.2664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Blowers | 31345 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 15831.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15831.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Membrane | 47118 | $/replacement | Replace at Lifespan | 10 | CAPDET, membrane | Equipment + Installation | 49018.8755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30372.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18646.1926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Permeate Pumps | 32115 | $/replacement | Replace at Lifespan | 25 | CAPDET, pumps | Equipment + Installation | 9957.8309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9957.8309 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Swing Arms | 57666 | $/replacement | Replace at Lifespan | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 22820.3944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22820.3944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Diffusers | 3801 | $/replacement | Replace at Lifespan | 10 | CADPET, fine diffuser | Equipment + Installation | 3954.3433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2450.1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1504.1848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | All MBR | Mixed WW | Materials | Materials | Fine Screen | Construction | 48966.2232 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 24731.2701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48966.2232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24731.2701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Materials | Materials | Equalization | Aerators | 40433.7165 | $/replacement | Replace at Lifespan | 15 | CAPDET, Aerators | Equipment + Installation | 20421.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40433.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20421.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | All MBR | Graywater | Materials | Materials | Equalization | Aerators | 33146.5444 | $/replacement | Replace at Lifespan | 15 | CAPDET, Aerators | Equipment + Installation | 16741.2574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33146.5444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16741.2574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | AeMBR | Blowers | 13680 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 6909.3296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6909.3296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | AeMBR | Membrane | 15078 | $/replacement | Replace at Lifespan | 10 | CAPDET, membrane | Equipment + Installation | 15686.2898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9719.4132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5966.8766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | AeMBR | Permeate Pumps | 19440 | $/replacement | Replace at Lifespan | 25 | CAPDET, pumps | Equipment + Installation | 6027.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6027.7202 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | AeMBR | Swing Arms | 48669.2015 | $/replacement | Replace at Lifespan | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 19260.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48669.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19260.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | AeMBR | Diffusers | 848 | $/replacement | Replace at Lifespan | 10 | CADPET, fine diffuser | Equipment + Installation | 882.2108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546.6284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335.5824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | Equalization | Aerators | 36773.6231 | $/replacement | Replace at Lifespan | 15 | CAPDET, Aerators | Equipment + Installation | 18573.1785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36773.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18573.1785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | All MBR | Graywater | Materials | Materials | Fine Screen | Construction | 36349.1574 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 18358.7945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36349.1574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18358.7945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | AeMBR | Blowers | 20051 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 10127.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10127.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | AeMBR | Membrane | 29213 | $/replacement | Replace at Lifespan | 10 | CAPDET, membrane | Equipment + Installation | 30391.5364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18830.9603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11560.5761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | AeMBR | Permeate Pumps | 26010 | $/replacement | Replace at Lifespan | 25 | CAPDET, pumps | Equipment + Installation | 8064.8663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8064.8663 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | AeMBR | Swing Arms | 57434 | $/replacement | Replace at Lifespan | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 22728.5841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22728.5841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | AeMBR | Diffusers | 1483 | $/replacement | Replace at Lifespan | 10 | CADPET, fine diffuser | Equipment + Installation | 1542.8285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 955.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586.8735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | AnMBR | membrane | 62823.7722 | $/replacement | Replace at Lifespan | 10 | CAPDET, membrane | Equipment + Installation | 65358.2637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62823.7722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62823.7722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40496.7637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24861.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | AnMBR | Permeate Pumps | 23670 | $/replacement | Replace at Lifespan | 25 | CAPDET, Pumps | Equipment + Installation | 7339.3074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7339.3074 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | AnMBR | Sludge Pump | 2592 | $/replacement | Replace at Lifespan | 25 | CAPDET, Pumps | Equipment + Installation | 803.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803.696 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | AnMBR | Biogas Recirculation Blower | 24595 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 12422.1463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12422.1463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | AnMBR | Mixers | 17455 | $/replacement | Replace at Lifespan | 15 | CAPDET, process equipment | Equipment + Installation | 8815.9611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8815.9611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Both | Materials | Materials | AnMBR | Gas Safety Equipment | 53426 | $/replacement | Replace at Lifespan | 15 | CAPDET, process equipment | Equipment + Installation | 26983.7605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26983.7605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | Materials | AeMBR | Sludge Pump | 3606 | $/replacement | Replace at Lifespan | 25 | CAPDET, Pumps | Equipment + Installation | 1118.1049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.1049 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | Zeolite | Feed System (pumps and piping | 15372.0212 | $/replacement | Replace at Lifespan | 25 | CAPDET, pumps | Equipment + Installation | 4766.3705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15372.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4766.3705 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | Zeolite | Regeneration System | 19265.0881 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 9730.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19265.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9730.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | Zeolite | Zeolite Replacement System | 27632.3545 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 13956.2167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27632.3545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13956.2167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | AeMBR | Sludge Pump | 2349 | $/replacement | Replace at Lifespan | 25 | CAPDET, Pumps | Equipment + Installation | 728.3495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728.3495 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | Materials | Fine Screen | Construction | 70633.0501 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 35674.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70633.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35674.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | Materials | Fine Screen | Construction | 53481.0516 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 27011.5653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53481.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27011.5653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | AnMBR | membrane | 40207.2531 | $/replacement | Replace at Lifespan | 10 | CAPDET, membrane | Equipment + Installation | 41829.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40207.2531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40207.2531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25917.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15911.3754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | AnMBR | Permeate Pumps | 19440 | $/replacement | Replace at Lifespan | 25 | CAPDET, Pumps | Equipment + Installation | 6027.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6027.7202 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | AnMBR | Sludge Pump | 2211 | $/replacement | Replace at Lifespan | 25 | CAPDET, Pumps | Equipment + Installation | 685.5601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.5601 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | AnMBR | Biogas Recirculation Blower | 18676 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 9432.6491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9432.6491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | AnMBR | Mixers | 16260 | $/replacement | Replace at Lifespan | 15 | CAPDET, process equipment | Equipment + Installation | 8212.4049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8212.4049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | DHS | Blower | 2046 | $/replacement | Replace at Lifespan | 15 | CAPDET, process equipment | Equipment + Installation | 1033.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1033.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Mixed WW | Materials | Materials | DHS | Sponge Media | 15378 | $/replacement | Replace at Lifespan | 10 | CAPDET, membrane | Equipment + Installation | 15998.3927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9912.7959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6085.5968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | DHS | Blower | 1553 | $/replacement | Replace at Lifespan | 15 | CAPDET, process equipment | Equipment + Installation | 784.3705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784.3705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | DHS | Sponge Media | 9842 | $/replacement | Replace at Lifespan | 10 | CAPDET, membrane | Equipment + Installation | 10239.0546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6344.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3894.8136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | Zeolite | Feed System (pumps and piping | 11760.8567 | $/replacement | Replace at Lifespan | 25 | CAPDET, pumps | Equipment + Installation | 3646.6643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11760.8567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3646.6643 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | Zeolite | Regeneration System | 16259.9569 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 8212.3831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16259.9569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8212.3831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AnMBR | Graywater | Materials | Materials | Zeolite | Zeolite Replacement System | 24386.4332 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 12316.8059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24386.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12316.8059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Both | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Sludge Pump | 4860 | $/replacement | Replace at Lifespan | 25 | CAPDET, pumps | Equipment + Installation | 1506.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1506.93 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | AeMBR | Sludge Pump | 3143 | $/replacement | Replace at Lifespan | 25 | CAPDET, pumps | Equipment + Installation | 974.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 974.5434 | 0 | 0 | 0 | 0 | 0
|  | Both | Unsewered | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Diffusers | 3918 | $/replacement | Replace at Lifespan | 10 | CADPET, fine diffuser | Equipment + Installation | 4076.0634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2525.5777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1550.4856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Unsewered | District | AeMBR | Mixed WW | Materials | Materials | AeMBR | Swing Arms | 57678 | $/replacement | Replace at Lifespan | 20 | CAPDET, swing arm diffuser | Equipment + Installation | 22825.1432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22825.1432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Unsewered | District | AeMBR | Mixed WW | Materials | Materials | Dewatering | Equipment + Install | 66800 | $/replacement | Replace at Lifespan | 15 | CAPDET, process Equipment | Equipment + Installation | 33738.5393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33738.5393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Materials | Materials | Clarification | Sludge Pump | 3928 | $/replacement | Replace at Lifespan | 25 | CAPDET, Pumps | Equipment + Installation | 1217.9468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1217.9468 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Graywater | Materials | Materials | Clarification | Sludge Pump | 2219 | $/replacement | Replace at Lifespan | 25 | CAPDET, Pumps | Equipment + Installation | 688.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 688.0407 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Sewered | Building | All | Mixed WW | Materials | Materials | Building Reuse | Installed Pump Cost | 31805.933 | $/replacement | Replace at Lifespan | 25 | CAPDET | Equipment + Installation | 9861.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31805.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.9992 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Sewered | Building | All | Graywater | Materials | Materials | Building Reuse | Installed Pump Cost | 31805.933 | $/replacement | Replace at Lifespan | 25 | CAPDET | Equipment + Installation | 9861.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31805.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.9992 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Both | District | All | Mixed WW | Materials | Materials | Building Reuse | Installed Pump Cost | 86367 | $/replacement | Replace at Lifespan | 25 | CAPDET | Equipment + Installation | 26779.6352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26779.6352 | 0 | 0 | 0 | 0 | 0
|  | Low Reuse | Both | District | All | Graywater | Materials | Materials | Building Reuse | Installed Pump Cost | 86367 | $/replacement | Replace at Lifespan | 25 | CAPDET | Equipment + Installation | 26779.6352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26779.6352 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Sewered | Building | All | Mixed WW | Materials | Materials | Building Reuse | Installed Pump Cost | 46727.1379 | $/replacement | Replace at Lifespan | 25 | CAPDET | Equipment + Installation | 14488.586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46727.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14488.586 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Sewered | Building | All | Graywater | Materials | Materials | Building Reuse | Installed Pump Cost | 46412.1379 | $/replacement | Replace at Lifespan | 25 | CAPDET | Equipment + Installation | 14390.9146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46412.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14390.9146 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Both | District | All | Mixed WW | Materials | Materials | Building Reuse | Installed Pump Cost | 120517 | $/replacement | Replace at Lifespan | 25 | CAPDET | Equipment + Installation | 37368.4543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37368.4543 | 0 | 0 | 0 | 0 | 0
|  | High Reuse | Both | District | All | Graywater | Materials | Materials | Building Reuse | Installed Pump Cost | 120517 | $/replacement | Replace at Lifespan | 25 | CAPDET | Equipment + Installation | 37368.4543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37368.4543 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Mixed WW | Materials | Materials | Thermal Recovery | Heat Pump | 43765.0345 | $/replacement | Replace at Lifespan | 15 | CAPDET, mechanical equipment | Equipment + Installation | 22104.3164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43765.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22104.3164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | AeMBR | Graywater | Materials | Materials | Thermal Recovery | Heat Pump | 34485.6574 | $/replacement | Replace at Lifespan | 15 | CAPDET, mechanical equipment | Equipment + Installation | 17417.6004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34485.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17417.6004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Maintenance Labor | Ozone | General Maintenance | 1088.2575 | $/yr | Annual |  |  |  | 17565.6444 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1088.2575 | 1036.4357 | 987.0816 | 940.0777 | 895.3121 | 852.6782 | 812.0745 | 773.4043 | 736.5755 | 701.5005 | 668.0957 | 636.2816 | 605.9825 | 577.1262 | 549.644 | 523.4705 | 498.5433 | 474.8031 | 452.1935 | 430.6604 | 410.1528 | 390.6217 | 372.0207 | 354.3054 | 337.4337 | 321.3655 | 306.0623 | 291.4879 | 277.6076 | 264.3882
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Maintenance Labor | Wetland | Storage tank Maintanence | 90 | $/yr | Annual |  |  |  | 1452.6966 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 85.7143 | 81.6327 | 77.7454 | 74.0432 | 70.5174 | 67.1594 | 63.9613 | 60.9155 | 58.0148 | 55.2522 | 52.6211 | 50.1154 | 47.7289 | 45.4561 | 43.2915 | 41.23 | 39.2667 | 37.3969 | 35.6161 | 33.9201 | 32.3048 | 30.7665 | 29.3014 | 27.9061 | 26.5772 | 25.3117 | 24.1063 | 22.9584 | 21.8652
|  | Both | Sewered | Building | RVFW | Both | Labor | Maintenance Labor | UV | General Maintenance | 77.88 | $/yr | Annual |  |  |  | 1257.0668 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 74.1714 | 70.6395 | 67.2757 | 64.0721 | 61.021 | 58.1153 | 55.3479 | 52.7122 | 50.2021 | 47.8116 | 45.5348 | 43.3665 | 41.3014 | 39.3347 | 37.4616 | 35.6777 | 33.9788 | 32.3607 | 30.8198 | 29.3522 | 27.9544 | 26.6233 | 25.3555 | 24.1481 | 22.9982 | 21.903 | 20.86 | 19.8667 | 18.9207
|  | Both | Sewered | Building | All | Mixed WW | Labor | Maintenance Labor | Building Reuse | Storage tank Maintanence | 90 | $/yr | Annual |  |  |  | 1452.6966 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 85.7143 | 81.6327 | 77.7454 | 74.0432 | 70.5174 | 67.1594 | 63.9613 | 60.9155 | 58.0148 | 55.2522 | 52.6211 | 50.1154 | 47.7289 | 45.4561 | 43.2915 | 41.23 | 39.2667 | 37.3969 | 35.6161 | 33.9201 | 32.3048 | 30.7665 | 29.3014 | 27.9061 | 26.5772 | 25.3117 | 24.1063 | 22.9584 | 21.8652
|  | Both | Both | All | All | Both | Labor | Maintenance Labor | Chlorination | General Maintenance | 1608.2415 | $/yr | Annual |  |  |  | 25958.7442 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1608.2415 | 1531.6586 | 1458.7224 | 1389.2595 | 1323.1043 | 1260.0993 | 1200.0946 | 1142.9472 | 1088.5211 | 1036.6868 | 987.3208 | 940.3055 | 895.529 | 852.8848 | 812.2712 | 773.5917 | 736.754 | 701.6704 | 668.2576 | 636.4358 | 606.1293 | 577.266 | 549.7771 | 523.5973 | 498.6641 | 474.9182 | 452.303 | 430.7648 | 410.2522 | 390.7164
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Maintenance Labor | Clarification | General maintenance | 532.125 | $/yr | Annual |  |  |  | 8589.0688 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 532.125 | 506.7857 | 482.6531 | 459.6696 | 437.7806 | 416.9339 | 397.0799 | 378.1713 | 360.1631 | 343.0125 | 326.6786 | 311.1225 | 296.3071 | 282.1972 | 268.7593 | 255.9612 | 243.7726 | 232.1644 | 221.1089 | 210.5799 | 200.5523 | 191.0022 | 181.9069 | 173.2446 | 164.9949 | 157.138 | 149.6552 | 142.5288 | 135.7417 | 129.2778
|  | Both | Sewered | Building | All | Mixed WW | Labor | Maintenance Labor | Chlorination | Basin Maintenance | 25.2 | $/yr | Annual |  |  |  | 406.7551 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 24 | 22.8571 | 21.7687 | 20.7321 | 19.7449 | 18.8046 | 17.9092 | 17.0564 | 16.2441 | 15.4706 | 14.7339 | 14.0323 | 13.3641 | 12.7277 | 12.1216 | 11.5444 | 10.9947 | 10.4711 | 9.9725 | 9.4976 | 9.0453 | 8.6146 | 8.2044 | 7.8137 | 7.4416 | 7.0873 | 6.7498 | 6.4284 | 6.1222
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Maintenance Labor | Clarification | General maintenance | 354.75 | $/yr | Annual |  |  |  | 5726.0459 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 354.75 | 337.8571 | 321.7687 | 306.4464 | 291.8537 | 277.9559 | 264.7199 | 252.1142 | 240.1088 | 228.675 | 217.7857 | 207.415 | 197.5381 | 188.1315 | 179.1729 | 170.6408 | 162.5151 | 154.7762 | 147.406 | 140.3866 | 133.7015 | 127.3348 | 121.2712 | 115.4964 | 109.9966 | 104.7587 | 99.7702 | 95.0192 | 90.4945 | 86.1852
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Maintenance Labor | Wetland | Storage tank Maintanence | 60 | $/yr | Annual |  |  |  | 968.4644 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 57.1429 | 54.4218 | 51.8303 | 49.3621 | 47.0116 | 44.7729 | 42.6409 | 40.6104 | 38.6765 | 36.8348 | 35.0808 | 33.4102 | 31.8193 | 30.3041 | 28.861 | 27.4867 | 26.1778 | 24.9312 | 23.744 | 22.6134 | 21.5365 | 20.511 | 19.5343 | 18.6041 | 17.7182 | 16.8744 | 16.0709 | 15.3056 | 14.5768
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Maintenance Labor | Building Reuse | Storage tank Maintanence | 60 | $/yr | Annual |  |  |  | 968.4644 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 57.1429 | 54.4218 | 51.8303 | 49.3621 | 47.0116 | 44.7729 | 42.6409 | 40.6104 | 38.6765 | 36.8348 | 35.0808 | 33.4102 | 31.8193 | 30.3041 | 28.861 | 27.4867 | 26.1778 | 24.9312 | 23.744 | 22.6134 | 21.5365 | 20.511 | 19.5343 | 18.6041 | 17.7182 | 16.8744 | 16.0709 | 15.3056 | 14.5768
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Maintenance Labor | Equalization | Tank + Aerator | 1155.9829 | $/yr | Annual |  |  |  | 18658.8052 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1155.9829 | 1100.9361 | 1048.5106 | 998.5815 | 951.03 | 905.7429 | 862.6122 | 821.5355 | 782.4147 | 745.1569 | 709.6732 | 675.8793 | 643.6945 | 613.0424 | 583.8499 | 556.0475 | 529.5691 | 504.3515 | 480.3348 | 457.4617 | 435.6778 | 414.9312 | 395.1726 | 376.3549 | 358.4332 | 341.365 | 325.1095 | 309.6281 | 294.8839 | 280.8418
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Maintenance Labor | Equalization | Tank + Aerator | 1068.3203 | $/yr | Annual |  |  |  | 17243.8361 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1068.3203 | 1017.4479 | 968.998 | 922.8552 | 878.9097 | 837.0569 | 797.197 | 759.2353 | 723.0812 | 688.6488 | 655.856 | 624.6247 | 594.8807 | 566.553 | 539.5743 | 513.8803 | 489.4098 | 466.1046 | 443.9091 | 422.7706 | 402.6387 | 383.4654 | 365.2051 | 347.8144 | 331.2518 | 315.4779 | 300.4552 | 286.1478 | 272.5217 | 259.5445
|  | Both | Sewered | Building | All MBR | Mixed WW | Labor | Maintenance Labor | UV | General Maintenance | 37.98 | $/yr | Annual |  |  |  | 613.038 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 37.98 | 36.1714 | 34.449 | 32.8086 | 31.2462 | 29.7583 | 28.3413 | 26.9917 | 25.7064 | 24.4822 | 23.3164 | 22.2061 | 21.1487 | 20.1416 | 19.1825 | 18.269 | 17.3991 | 16.5705 | 15.7815 | 15.03 | 14.3143 | 13.6326 | 12.9835 | 12.3652 | 11.7764 | 11.2156 | 10.6815 | 10.1729 | 9.6885 | 9.2271
|  | Both | Sewered | Building | All MBR | Mixed WW | Labor | Maintenance Labor | Fine Screen | Maintenance | 794.7026 | $/yr | Annual |  |  |  | 12827.3527 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 794.7026 | 756.8596 | 720.8187 | 686.494 | 653.8038 | 622.6703 | 593.0193 | 564.7803 | 537.886 | 512.2724 | 487.8784 | 464.6461 | 442.5201 | 421.4477 | 401.3788 | 382.2655 | 364.0624 | 346.7261 | 330.2153 | 314.4908 | 299.515 | 285.2524 | 271.669 | 258.7324 | 246.4118 | 234.6779 | 223.5027 | 212.8597 | 202.7236 | 193.0701
|  | Both | Sewered | Building | All MBR | Graywater | Labor | Maintenance Labor | Fine Screen | Maintenance | 601.723 | $/yr | Annual |  |  |  | 9712.4549 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 601.723 | 573.0695 | 545.7805 | 519.7909 | 495.039 | 471.4657 | 449.015 | 427.6333 | 407.2698 | 387.876 | 369.4057 | 351.815 | 335.0619 | 319.1065 | 303.911 | 289.439 | 275.6562 | 262.5297 | 250.0283 | 238.1222 | 226.7831 | 215.9839 | 205.6989 | 195.9037 | 186.575 | 177.6905 | 169.229 | 161.1705 | 153.4957 | 146.1864
|  | Both | Sewered | Building | All MBR | Mixed WW | Labor | Maintenance Labor | Equalization | Tank + Aerator | 998.9694 | $/yr | Annual |  |  |  | 16124.438 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 998.9694 | 951.3994 | 906.0947 | 862.9473 | 821.8546 | 782.7186 | 745.4463 | 709.9489 | 676.1418 | 643.9446 | 613.2805 | 584.0767 | 556.2635 | 529.7748 | 504.5474 | 480.5213 | 457.6394 | 435.847 | 415.0924 | 395.3261 | 376.501 | 358.5724 | 341.4975 | 325.2358 | 309.7483 | 294.9984 | 280.9509 | 267.5723 | 254.8307 | 242.6959
|  | Both | Both | District | All MBR | Mixed WW | Labor | Maintenance Labor | Fine Screen | Maintenance | 1224.1556 | $/yr | Annual |  |  |  | 19759.1853 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1224.1556 | 1165.8625 | 1110.3452 | 1057.4716 | 1007.1158 | 959.1579 | 913.4837 | 869.9845 | 828.5567 | 789.1016 | 751.5253 | 715.7384 | 681.6556 | 649.1958 | 618.2818 | 588.8398 | 560.7998 | 534.095 | 508.6619 | 484.4399 | 461.3714 | 439.4013 | 418.4774 | 398.5499 | 379.5714 | 361.4965 | 344.2824 | 327.888 | 312.2743 | 297.4041
|  | Both | Both | District | AeMBR | Mixed WW | Labor | Maintenance Labor | Equalization | Tank + Aerator | 1209.8704 | $/yr | Annual |  |  |  | 19528.6073 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1209.8704 | 1152.2575 | 1097.3881 | 1045.1316 | 995.3634 | 947.9651 | 902.8239 | 859.8323 | 818.8879 | 779.8933 | 742.7555 | 707.3862 | 673.7011 | 641.6201 | 611.0668 | 581.9684 | 554.2556 | 527.8625 | 502.7261 | 478.7868 | 455.9874 | 434.2737 | 413.594 | 393.8991 | 375.142 | 357.2781 | 340.2648 | 324.0618 | 308.6302 | 293.9336
|  | Both | Both | District | AeMBR | Mixed WW | Labor | Maintenance Labor | Building Reuse | Storage tank Maintanence | 150 | $/yr | Annual |  |  |  | 2421.161 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 142.8571 | 136.0544 | 129.5756 | 123.4054 | 117.5289 | 111.9323 | 106.6022 | 101.5259 | 96.6913 | 92.087 | 87.7019 | 83.5256 | 79.5482 | 75.7602 | 72.1526 | 68.7167 | 65.4445 | 62.3281 | 59.3601 | 56.5334 | 53.8414 | 51.2775 | 48.8357 | 46.5102 | 44.2954 | 42.1861 | 40.1772 | 38.264 | 36.4419
|  | Both | Both | District | All MBR | Both | Labor | Maintenance Labor | UV | General Maintenance | 77.88 | $/yr | Annual |  |  |  | 1257.0668 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 77.88 | 74.1714 | 70.6395 | 67.2757 | 64.0721 | 61.021 | 58.1153 | 55.3479 | 52.7122 | 50.2021 | 47.8116 | 45.5348 | 43.3665 | 41.3014 | 39.3347 | 37.4616 | 35.6777 | 33.9788 | 32.3607 | 30.8198 | 29.3522 | 27.9544 | 26.6233 | 25.3555 | 24.1481 | 22.9982 | 21.903 | 20.86 | 19.8667 | 18.9207
|  | Both | Sewered | Building | AeMBR | Graywater | Labor | Maintenance Labor | UV | General Maintenance | 31.26 | $/yr | Annual |  |  |  | 504.57 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 29.7714 | 28.3537 | 27.0036 | 25.7177 | 24.493 | 23.3267 | 22.2159 | 21.158 | 20.1505 | 19.1909 | 18.2771 | 17.4067 | 16.5778 | 15.7884 | 15.0366 | 14.3206 | 13.6386 | 12.9892 | 12.3706 | 11.7816 | 11.2205 | 10.6862 | 10.1774 | 9.6927 | 9.2312 | 8.7916 | 8.3729 | 7.9742 | 7.5945
|  | Both | Sewered | Building | All MBR | Graywater | Labor | Maintenance Labor | Building Reuse | Storage tank Maintanence | 60 | $/yr | Annual |  |  |  | 968.4644 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 57.1429 | 54.4218 | 51.8303 | 49.3621 | 47.0116 | 44.7729 | 42.6409 | 40.6104 | 38.6765 | 36.8348 | 35.0808 | 33.4102 | 31.8193 | 30.3041 | 28.861 | 27.4867 | 26.1778 | 24.9312 | 23.744 | 22.6134 | 21.5365 | 20.511 | 19.5343 | 18.6041 | 17.7182 | 16.8744 | 16.0709 | 15.3056 | 14.5768
|  | Both | Sewered | Building | All MBR | Graywater | Labor | Maintenance Labor | Equalization | Tank + Aerator | 915.1236 | $/yr | Annual |  |  |  | 14771.0775 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 915.1236 | 871.5463 | 830.0441 | 790.5182 | 752.8745 | 717.0233 | 682.8793 | 650.3613 | 619.3917 | 589.8968 | 561.8065 | 535.0538 | 509.5751 | 485.3096 | 462.1996 | 440.1901 | 419.2287 | 399.2654 | 380.2528 | 362.1455 | 344.9005 | 328.4766 | 312.8349 | 297.938 | 283.7505 | 270.2385 | 257.37 | 245.1143 | 233.4422 | 222.3259
|  | Both | Sewered | District | AeMBR | Graywater | Labor | Maintenance Labor | Equalization | Tank + Aerator | 1069.2431 | $/yr | Annual |  |  |  | 17258.7312 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1069.2431 | 1018.3267 | 969.835 | 923.6524 | 879.6689 | 837.7799 | 797.8856 | 759.8911 | 723.7058 | 689.2436 | 656.4225 | 625.1643 | 595.3946 | 567.0424 | 540.0404 | 514.3242 | 489.8326 | 466.5072 | 444.2926 | 423.1358 | 402.9865 | 383.7966 | 365.5206 | 348.1149 | 331.538 | 315.7504 | 300.7147 | 286.395 | 272.7571 | 259.7687
|  | Both | Sewered | District | AeMBR | Graywater | Labor | Maintenance Labor | Building Reuse | Storage tank Maintanence | 120 | $/yr | Annual |  |  |  | 1936.9288 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 114.2857 | 108.8435 | 103.6605 | 98.7243 | 94.0231 | 89.5458 | 85.2818 | 81.2207 | 77.3531 | 73.6696 | 70.1615 | 66.8205 | 63.6386 | 60.6082 | 57.7221 | 54.9734 | 52.3556 | 49.8625 | 47.4881 | 45.2267 | 43.0731 | 41.022 | 39.0686 | 37.2081 | 35.4363 | 33.7489 | 32.1418 | 30.6112 | 29.1536
|  | Both | Sewered | District | All MBR | Graywater | Labor | Maintenance Labor | Fine Screen | Maintenance | 908.7289 | $/yr | Annual |  |  |  | 14667.8606 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 908.7289 | 865.4561 | 824.2439 | 784.9942 | 747.6135 | 712.0129 | 678.1075 | 645.8167 | 615.0635 | 585.7748 | 557.8807 | 531.315 | 506.0143 | 481.9184 | 458.9699 | 437.1142 | 416.2992 | 396.4754 | 377.5956 | 359.6149 | 342.4904 | 326.1813 | 310.6489 | 295.8561 | 281.7677 | 268.3502 | 255.5716 | 243.4015 | 231.811 | 220.7724
|  | Both | Sewered | Building | AnMBR | Mixed WW | Labor | Maintenance Labor | Zeolite | Maintenance materials | 989.9619 | $/yr | Annual |  |  |  | 15979.0481 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 989.9619 | 942.8209 | 897.9246 | 855.1663 | 814.4441 | 775.6611 | 738.7248 | 703.5474 | 670.0452 | 638.1383 | 607.7507 | 578.8102 | 551.2478 | 524.9979 | 499.998 | 476.1886 | 453.513 | 431.9171 | 411.3496 | 391.7615 | 373.1062 | 355.3393 | 338.4184 | 322.3032 | 306.9554 | 292.3385 | 278.4176 | 265.1596 | 252.533 | 240.5076
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Maintenance Labor | Fine Screen | Maintenance | 1765.8263 | $/yr | Annual |  |  |  | 28502.3315 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1765.8263 | 1681.7393 | 1601.6565 | 1525.3871 | 1452.7496 | 1383.5711 | 1317.6867 | 1254.9398 | 1195.1807 | 1138.2673 | 1084.0641 | 1032.442 | 983.2781 | 936.4554 | 891.8623 | 849.3926 | 808.9454 | 770.4241 | 733.7373 | 698.7974 | 665.5213 | 633.8299 | 603.6475 | 574.9024 | 547.5261 | 521.4534 | 496.6223 | 472.9736 | 450.451 | 429.001
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Maintenance Labor | Fine Screen | Maintenance | 1337.0263 | $/yr | Annual |  |  |  | 21581.0397 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1337.0263 | 1273.3584 | 1212.7223 | 1154.9736 | 1099.9748 | 1047.5951 | 997.7096 | 950.1996 | 904.952 | 861.8591 | 820.8182 | 781.7316 | 744.5063 | 709.0536 | 675.2891 | 643.1325 | 612.5071 | 583.3401 | 555.562 | 529.1067 | 503.9111 | 479.9154 | 457.0623 | 435.2974 | 414.5689 | 394.8276 | 376.0263 | 358.1202 | 341.0669 | 324.8256
|  | Both | Sewered | Building | AnMBR | Graywater | Labor | Maintenance Labor | UV | General Maintenance | 31.26 | $/yr | Annual |  |  |  | 504.57 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 31.26 | 29.7714 | 28.3537 | 27.0036 | 25.7177 | 24.493 | 23.3267 | 22.2159 | 21.158 | 20.1505 | 19.1909 | 18.2771 | 17.4067 | 16.5778 | 15.7884 | 15.0366 | 14.3206 | 13.6386 | 12.9892 | 12.3706 | 11.7816 | 11.2205 | 10.6862 | 10.1774 | 9.6927 | 9.2312 | 8.7916 | 8.3729 | 7.9742 | 7.5945
|  | Both | Unsewered | District | AeMBR | Mixed WW | Labor | Maintenance Labor | Dewatering | Material and Labor | 1670 | $/yr | Annual |  |  |  | 26955.5929 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1670 | 1590.4762 | 1514.7392 | 1442.6088 | 1373.9131 | 1308.4887 | 1246.1797 | 1186.8378 | 1130.3217 | 1076.4969 | 1025.2351 | 976.4144 | 929.9185 | 885.6367 | 843.4635 | 803.2986 | 765.0462 | 728.6155 | 693.9195 | 660.8757 | 629.4054 | 599.4337 | 570.8893 | 543.7041 | 517.8134 | 493.1556 | 469.672 | 447.3067 | 426.0064 | 405.7204
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Maintenance Labor | Clarification | Sludge Pump | 98.2 | $/yr | Annual |  |  |  | 1585.0534 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 93.5238 | 89.0703 | 84.8289 | 80.7894 | 76.9423 | 73.2784 | 69.7889 | 66.4656 | 63.3006 | 60.2863 | 57.4155 | 54.6814 | 52.0776 | 49.5977 | 47.2359 | 44.9866 | 42.8443 | 40.8041 | 38.8611 | 37.0105 | 35.2481 | 33.5697 | 31.9711 | 30.4487 | 28.9987 | 27.6178 | 26.3027 | 25.0502 | 23.8573
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Maintenance Labor | Clarification | Sludge Pump | 55.475 | $/yr | Annual |  |  |  | 895.4261 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 55.475 | 52.8333 | 50.3175 | 47.9214 | 45.6394 | 43.4661 | 41.3963 | 39.425 | 37.5477 | 35.7597 | 34.0568 | 32.4351 | 30.8906 | 29.4196 | 28.0186 | 26.6844 | 25.4137 | 24.2036 | 23.051 | 21.9533 | 20.9079 | 19.9123 | 18.9641 | 18.0611 | 17.201 | 16.3819 | 15.6018 | 14.8589 | 14.1513 | 13.4774
|  | Both | Sewered | Building | RVFW | Mixed WW | Labor | Maintenance Labor | Wetland | Pumps | 3181.925 | $/yr | Annual |  |  |  | 51359.6855 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3181.925 | 3030.4048 | 2886.0998 | 2748.6665 | 2617.7776 | 2493.1215 | 2374.4014 | 2261.3347 | 2153.6521 | 2051.0972 | 1953.4259 | 1860.4056 | 1771.8149 | 1687.4428 | 1607.0883 | 1530.5603 | 1457.6765 | 1388.2633 | 1322.1556 | 1259.1958 | 1199.2341 | 1142.1277 | 1087.7407 | 1035.9435 | 986.6128 | 939.6313 | 894.8869 | 852.2733 | 811.6888 | 773.037
|  | Both | Sewered | Building | RVFW | Graywater | Labor | Maintenance Labor | Wetland | Pumps | 2121.275 | $/yr | Annual |  |  |  | 34239.6559 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2121.275 | 2020.2619 | 1924.059 | 1832.4371 | 1745.1782 | 1662.0745 | 1582.9281 | 1507.5505 | 1435.7624 | 1367.3928 | 1302.2788 | 1240.2656 | 1181.2053 | 1124.9574 | 1071.388 | 1020.3695 | 971.7805 | 925.5053 | 881.4336 | 839.4605 | 799.4862 | 761.4155 | 725.1576 | 690.6263 | 657.7393 | 626.4184 | 596.5889 | 568.1799 | 541.1238 | 515.356
|  | Low Reuse | Sewered | Building | All | Mixed WW | Labor | Maintenance Labor | Building Reuse | Pipe maintenance | 2350.515 | $/yr | Annual |  |  |  | 37939.8356 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2238.5857 | 2131.9864 | 2030.4632 | 1933.7745 | 1841.69 | 1753.9905 | 1670.4671 | 1590.9211 | 1515.1629 | 1443.0123 | 1374.2974 | 1308.8547 | 1246.5283 | 1187.1698 | 1130.6379 | 1076.798 | 1025.5219 | 976.6875 | 930.1786 | 885.8844 | 843.6994 | 803.5232 | 765.2602 | 728.8193 | 694.1136 | 661.0606 | 629.5815 | 599.6014 | 571.049
|  | Low Reuse | Sewered | Building | All | Graywater | Labor | Maintenance Labor | Building Reuse | Pipe maintenance | 4701.0225 | $/yr | Annual |  |  |  | 75879.5501 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4477.1643 | 4263.966 | 4060.92 | 3867.5428 | 3683.3741 | 3507.9754 | 3340.9289 | 3181.8371 | 3030.321 | 2886.02 | 2748.5905 | 2617.7052 | 2493.0526 | 2374.3358 | 2261.2722 | 2153.5926 | 2051.0405 | 1953.3719 | 1860.3542 | 1771.7659 | 1687.3961 | 1607.0439 | 1530.518 | 1457.6362 | 1388.225 | 1322.119 | 1259.161 | 1199.2009 | 1142.0961
|  | Low Reuse | Both | District | All | Mixed WW | Labor | Maintenance Labor | Building Reuse | Pipe maintenance | 4600.6575 | $/yr | Annual |  |  |  | 74259.5512 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4381.5786 | 4172.932 | 3974.2209 | 3784.9723 | 3604.7355 | 3433.0815 | 3269.6014 | 3113.9061 | 2965.6248 | 2824.4046 | 2689.9092 | 2561.8182 | 2439.8269 | 2323.6447 | 2212.9949 | 2107.6142 | 2007.2516 | 1911.6682 | 1820.6364 | 1733.9394 | 1651.3709 | 1572.7342 | 1497.8421 | 1426.5163 | 1358.5869 | 1293.8923 | 1232.2784 | 1173.5985 | 1117.7128
|  | Low Reuse | Both | District | All | Graywater | Labor | Maintenance Labor | Building Reuse | Pipe maintenance | 9201.3225 | $/yr | Annual |  |  |  | 148519.2235 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 8763.1643 | 8345.8707 | 7948.4483 | 7569.9508 | 7209.4769 | 6866.1685 | 6539.2081 | 6227.8173 | 5931.2545 | 5648.8138 | 5379.8227 | 5123.6407 | 4879.6578 | 4647.2931 | 4425.9934 | 4215.2319 | 4014.5065 | 3823.3396 | 3641.2758 | 3467.8817 | 3302.7445 | 3145.4709 | 2995.6866 | 2853.0348 | 2717.176 | 2587.7867 | 2464.5588 | 2347.1988 | 2235.4275
|  | High Reuse | Sewered | Building | All | Mixed WW | Labor | Maintenance Labor | Building Reuse | Pipe maintenance | 2350.515 | $/yr | Annual |  |  |  | 37939.8356 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2350.515 | 2238.5857 | 2131.9864 | 2030.4632 | 1933.7745 | 1841.69 | 1753.9905 | 1670.4671 | 1590.9211 | 1515.1629 | 1443.0123 | 1374.2974 | 1308.8547 | 1246.5283 | 1187.1698 | 1130.6379 | 1076.798 | 1025.5219 | 976.6875 | 930.1786 | 885.8844 | 843.6994 | 803.5232 | 765.2602 | 728.8193 | 694.1136 | 661.0606 | 629.5815 | 599.6014 | 571.049
|  | High Reuse | Sewered | Building | All | Graywater | Labor | Maintenance Labor | Building Reuse | Pipe maintenance | 4701.0225 | $/yr | Annual |  |  |  | 75879.5501 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4701.0225 | 4477.1643 | 4263.966 | 4060.92 | 3867.5428 | 3683.3741 | 3507.9754 | 3340.9289 | 3181.8371 | 3030.321 | 2886.02 | 2748.5905 | 2617.7052 | 2493.0526 | 2374.3358 | 2261.2722 | 2153.5926 | 2051.0405 | 1953.3719 | 1860.3542 | 1771.7659 | 1687.3961 | 1607.0439 | 1530.518 | 1457.6362 | 1388.225 | 1322.119 | 1259.161 | 1199.2009 | 1142.0961
|  | High Reuse | Both | District | All | Mixed WW | Labor | Maintenance Labor | Building Reuse | Pipe maintenance | 4600.6575 | $/yr | Annual |  |  |  | 74259.5512 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4600.6575 | 4381.5786 | 4172.932 | 3974.2209 | 3784.9723 | 3604.7355 | 3433.0815 | 3269.6014 | 3113.9061 | 2965.6248 | 2824.4046 | 2689.9092 | 2561.8182 | 2439.8269 | 2323.6447 | 2212.9949 | 2107.6142 | 2007.2516 | 1911.6682 | 1820.6364 | 1733.9394 | 1651.3709 | 1572.7342 | 1497.8421 | 1426.5163 | 1358.5869 | 1293.8923 | 1232.2784 | 1173.5985 | 1117.7128
|  | High Reuse | Both | District | All | Graywater | Labor | Maintenance Labor | Building Reuse | Pipe maintenance | 9201.3225 | $/yr | Annual |  |  |  | 148519.2235 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 9201.3225 | 8763.1643 | 8345.8707 | 7948.4483 | 7569.9508 | 7209.4769 | 6866.1685 | 6539.2081 | 6227.8173 | 5931.2545 | 5648.8138 | 5379.8227 | 5123.6407 | 4879.6578 | 4647.2931 | 4425.9934 | 4215.2319 | 4014.5065 | 3823.3396 | 3641.2758 | 3467.8817 | 3302.7445 | 3145.4709 | 2995.6866 | 2853.0348 | 2717.176 | 2587.7867 | 2464.5588 | 2347.1988 | 2235.4275
|  | Low Reuse | Sewered | Building | All | Mixed WW | Labor | Maintenance Labor | Building Reuse | Pump Maintenance | 795.1483 | $/yr | Annual |  |  |  | 12834.5476 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 757.2841 | 721.223 | 686.879 | 654.1705 | 623.0195 | 593.3519 | 565.0971 | 538.1877 | 512.5597 | 488.1521 | 464.9068 | 442.7683 | 421.6841 | 401.6039 | 382.4799 | 364.2666 | 346.9206 | 330.4006 | 314.6672 | 299.683 | 285.4124 | 271.8214 | 258.8775 | 246.55 | 234.8095 | 223.6281 | 212.9791 | 202.8373 | 193.1784
|  | Low Reuse | Sewered | Building | All | Graywater | Labor | Maintenance Labor | Building Reuse | Pump Maintenance | 795.1483 | $/yr | Annual |  |  |  | 12834.5476 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 795.1483 | 757.2841 | 721.223 | 686.879 | 654.1705 | 623.0195 | 593.3519 | 565.0971 | 538.1877 | 512.5597 | 488.1521 | 464.9068 | 442.7683 | 421.6841 | 401.6039 | 382.4799 | 364.2666 | 346.9206 | 330.4006 | 314.6672 | 299.683 | 285.4124 | 271.8214 | 258.8775 | 246.55 | 234.8095 | 223.6281 | 212.9791 | 202.8373 | 193.1784
|  | Low Reuse | Both | District | All | Mixed WW | Labor | Maintenance Labor | Building Reuse | Pump Maintenance | 2159.175 | $/yr | Annual |  |  |  | 34851.4025 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2056.3571 | 1958.4354 | 1865.1765 | 1776.3586 | 1691.7701 | 1611.2096 | 1534.4854 | 1461.4146 | 1391.8235 | 1325.5461 | 1262.4249 | 1202.3094 | 1145.0566 | 1090.5301 | 1038.6001 | 989.1429 | 942.0409 | 897.1818 | 854.4589 | 813.7703 | 775.0194 | 738.1137 | 702.9654 | 669.4909 | 637.6104 | 607.248 | 578.3314 | 550.7918 | 524.5636
|  | Low Reuse | Both | District | All | Graywater | Labor | Maintenance Labor | Building Reuse | Pump Maintenance | 2159.175 | $/yr | Annual |  |  |  | 34851.4025 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2159.175 | 2056.3571 | 1958.4354 | 1865.1765 | 1776.3586 | 1691.7701 | 1611.2096 | 1534.4854 | 1461.4146 | 1391.8235 | 1325.5461 | 1262.4249 | 1202.3094 | 1145.0566 | 1090.5301 | 1038.6001 | 989.1429 | 942.0409 | 897.1818 | 854.4589 | 813.7703 | 775.0194 | 738.1137 | 702.9654 | 669.4909 | 637.6104 | 607.248 | 578.3314 | 550.7918 | 524.5636
|  | High Reuse | Sewered | Building | All | Mixed WW | Labor | Maintenance Labor | Building Reuse | Pump Maintenance | 1168.1784 | $/yr | Annual |  |  |  | 18855.6543 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1168.1784 | 1112.5509 | 1059.5723 | 1009.1165 | 961.0633 | 915.2984 | 871.7127 | 830.2026 | 790.6692 | 753.0182 | 717.1602 | 683.0097 | 650.4855 | 619.51 | 590.0095 | 561.9138 | 535.156 | 509.6724 | 485.4023 | 462.2879 | 440.2742 | 419.3087 | 399.3417 | 380.3254 | 362.2146 | 344.9663 | 328.5394 | 312.8946 | 297.9949 | 283.8047
|  | High Reuse | Sewered | Building | All | Graywater | Labor | Maintenance Labor | Building Reuse | Pump Maintenance | 1160.3034 | $/yr | Annual |  |  |  | 18728.5433 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1160.3034 | 1105.0509 | 1052.4294 | 1002.3137 | 954.5845 | 909.1281 | 865.8363 | 824.606 | 785.339 | 747.9419 | 712.3257 | 678.4054 | 646.1004 | 615.3337 | 586.0321 | 558.1258 | 531.5484 | 506.2366 | 482.13 | 459.1715 | 437.3062 | 416.4821 | 396.6496 | 377.7615 | 359.7729 | 342.6408 | 326.3246 | 310.7853 | 295.986 | 281.8915
|  | High Reuse | Both | District | All | Mixed WW | Labor | Maintenance Labor | Building Reuse | Pump Maintenance | 3012.925 | $/yr | Annual |  |  |  | 48631.8441 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 2869.4524 | 2732.8118 | 2602.6779 | 2478.7409 | 2360.7056 | 2248.291 | 2141.2295 | 2039.2662 | 1942.1583 | 1849.6746 | 1761.5948 | 1677.7094 | 1597.8185 | 1521.7319 | 1449.2684 | 1380.2557 | 1314.5292 | 1251.9326 | 1192.3167 | 1135.5397 | 1081.4664 | 1029.968 | 980.9219 | 934.2114 | 889.7251 | 847.3572 | 807.0069 | 768.578 | 731.979
|  | High Reuse | Both | District | All | Graywater | Labor | Maintenance Labor | Building Reuse | Pump Maintenance | 3012.925 | $/yr | Annual |  |  |  | 48631.8441 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 3012.925 | 2869.4524 | 2732.8118 | 2602.6779 | 2478.7409 | 2360.7056 | 2248.291 | 2141.2295 | 2039.2662 | 1942.1583 | 1849.6746 | 1761.5948 | 1677.7094 | 1597.8185 | 1521.7319 | 1449.2684 | 1380.2557 | 1314.5292 | 1251.9326 | 1192.3167 | 1135.5397 | 1081.4664 | 1029.968 | 980.9219 | 934.2114 | 889.7251 | 847.3572 | 807.0069 | 768.578 | 731.979
|  | Both | Sewered | Building | AeMBR | Mixed WW | Labor | Maintenance Labor | Thermal Recovery | Heat Pump Maintenance | 1094.1259 | $/yr | Annual |  |  |  | 17660.3661 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1094.1259 | 1042.0246 | 992.4044 | 945.1471 | 900.1401 | 857.2762 | 816.4536 | 777.5748 | 740.5475 | 705.2833 | 671.6984 | 639.7127 | 609.2502 | 580.2383 | 552.6079 | 526.2932 | 501.2317 | 477.3635 | 454.6319 | 432.9828 | 412.3645 | 392.7281 | 374.0268 | 356.216 | 339.2533 | 323.0984 | 307.7128 | 293.0598 | 279.1045 | 265.8139
|  | Both | Sewered | Building | AeMBR | Graywater | Labor | Maintenance Labor | Thermal Recovery | Heat Pump Maintenance | 862.1414 | $/yr | Annual |  |  |  | 13915.8883 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 862.1414 | 821.0871 | 781.9877 | 744.7502 | 709.2859 | 675.5104 | 643.3432 | 612.7078 | 583.5313 | 555.7441 | 529.2801 | 504.0762 | 480.0726 | 457.212 | 435.44 | 414.7048 | 394.9569 | 376.1495 | 358.2376 | 341.1786 | 324.932 | 309.4591 | 294.7229 | 280.6885 | 267.3224 | 254.5928 | 242.4693 | 230.9231 | 219.9268 | 209.4541
|  | Low Reuse | Both | Building | All | Mixed WW | Materials | Water | Avoided Utility Costs | Reduction in collective potable water cost for building | -25036.3636 | $/yr | Annual |  |  |  | -404113.7876 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -23844.1558 | -22708.7199 | -21627.3522 | -20597.4783 | -19616.646 | -18682.52 | -17792.8762 | -16945.5964 | -16138.6632 | -15370.1555 | -14638.2433 | -13941.1841 | -13277.3182 | -12645.0649 | -12042.919 | -11469.4467 | -10923.2825 | -10403.1262 | -9907.7393 | -9435.9421 | -8986.6116 | -8558.6777 | -8151.1216 | -7762.973 | -7393.3076 | -7041.2453 | -6705.9479 | -6386.6171 | -6082.4924
|  | High Reuse | Both | Building | All | Mixed WW | Materials | Water | Avoided Utility Costs | Reduction in collective potable water cost for building | -51165.7754 | $/yr | Annual |  |  |  | -825870.5454 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -48729.3099 | -46408.8666 | -44198.9205 | -42094.21 | -40089.7239 | -38180.6894 | -36362.5613 | -34631.0108 | -32981.915 | -31411.3476 | -29915.5692 | -28491.0183 | -27134.3031 | -25842.1934 | -24611.6128 | -23439.6312 | -22323.4583 | -21260.4365 | -20248.0348 | -19283.8426 | -18365.5644 | -17491.0137 | -16658.1083 | -15864.8651 | -15109.3953 | -14389.9003 | -13704.6669 | -13052.0637 | -12430.5369
|  | Low Reuse | Both | District | All | Mixed WW | Materials | Water | Avoided Utility Costs | Reduction in collective potable water cost for building | -49499.3316 | $/yr | Annual |  |  |  | -798972.3526 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -47142.2205 | -44897.3529 | -42759.3837 | -40723.2226 | -38784.0215 | -36937.1633 | -35178.2508 | -33503.096 | -31907.7105 | -30388.2957 | -28941.234 | -27563.08 | -26250.5524 | -25000.5261 | -23810.0248 | -22676.2141 | -21596.3944 | -20567.9947 | -19588.5663 | -18655.7775 | -17767.4071 | -16921.3401 | -16115.562 | -15348.1543 | -14617.2898 | -13921.2284 | -13258.3127 | -12626.9645 | -12025.6805
|  | High Reuse | Both | District | All | Mixed WW | Materials | Water | Avoided Utility Costs | Reduction in collective potable water cost for building | -104310.1604 | $/yr | Annual |  |  |  | -1683677.9744 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -99343.0099 | -94612.3904 | -90107.0385 | -85816.2271 | -81729.7401 | -77837.8477 | -74131.2836 | -70601.2224 | -67239.2595 | -64037.39 | -60987.9904 | -58083.8004 | -55317.9052 | -52683.7192 | -50174.9707 | -47785.6864 | -45510.1775 | -43343.0262 | -41279.0725 | -39313.4024 | -37441.3356 | -35658.4149 | -33960.3951 | -32343.2335 | -30803.0795 | -29336.2662 | -27939.3011 | -26608.8582 | -25341.7697
|  | Low Reuse | Both | Building | All | Graywater | Materials | Water | Avoided Utility Costs | Reduction in collective potable water cost for building | -25036.3636 | $/yr | Annual |  |  |  | -404113.7876 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -25036.3636 | -23844.1558 | -22708.7199 | -21627.3522 | -20597.4783 | -19616.646 | -18682.52 | -17792.8762 | -16945.5964 | -16138.6632 | -15370.1555 | -14638.2433 | -13941.1841 | -13277.3182 | -12645.0649 | -12042.919 | -11469.4467 | -10923.2825 | -10403.1262 | -9907.7393 | -9435.9421 | -8986.6116 | -8558.6777 | -8151.1216 | -7762.973 | -7393.3076 | -7041.2453 | -6705.9479 | -6386.6171 | -6082.4924
|  | High Reuse | Both | Building | All | Graywater | Materials | Water | Avoided Utility Costs | Reduction in collective potable water cost for building | -51165.7754 | $/yr | Annual |  |  |  | -825870.5454 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -51165.7754 | -48729.3099 | -46408.8666 | -44198.9205 | -42094.21 | -40089.7239 | -38180.6894 | -36362.5613 | -34631.0108 | -32981.915 | -31411.3476 | -29915.5692 | -28491.0183 | -27134.3031 | -25842.1934 | -24611.6128 | -23439.6312 | -22323.4583 | -21260.4365 | -20248.0348 | -19283.8426 | -18365.5644 | -17491.0137 | -16658.1083 | -15864.8651 | -15109.3953 | -14389.9003 | -13704.6669 | -13052.0637 | -12430.5369
|  | Low Reuse | Both | District | All | Graywater | Materials | Water | Avoided Utility Costs | Reduction in collective potable water cost for building | -49499.3316 | $/yr | Annual |  |  |  | -798972.3526 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -49499.3316 | -47142.2205 | -44897.3529 | -42759.3837 | -40723.2226 | -38784.0215 | -36937.1633 | -35178.2508 | -33503.096 | -31907.7105 | -30388.2957 | -28941.234 | -27563.08 | -26250.5524 | -25000.5261 | -23810.0248 | -22676.2141 | -21596.3944 | -20567.9947 | -19588.5663 | -18655.7775 | -17767.4071 | -16921.3401 | -16115.562 | -15348.1543 | -14617.2898 | -13921.2284 | -13258.3127 | -12626.9645 | -12025.6805
|  | High Reuse | Both | District | All | Graywater | Materials | Water | Avoided Utility Costs | Reduction in collective potable water cost for building | -104310.1604 | $/yr | Annual |  |  |  | -1683677.9744 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -104310.1604 | -99343.0099 | -94612.3904 | -90107.0385 | -85816.2271 | -81729.7401 | -77837.8477 | -74131.2836 | -70601.2224 | -67239.2595 | -64037.39 | -60987.9904 | -58083.8004 | -55317.9052 | -52683.7192 | -50174.9707 | -47785.6864 | -45510.1775 | -43343.0262 | -41279.0725 | -39313.4024 | -37441.3356 | -35658.4149 | -33960.3951 | -32343.2335 | -30803.0795 | -29336.2662 | -27939.3011 | -26608.8582 | -25341.7697
|  | Both | Both | Building | All | Mixed WW | Materials | Water | Avoided Utility Costs | Reduction in collective wastewater cost for building | -121049.4652 | $/yr | Annual |  |  |  | -1953868.3251 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -121049.4652 | -115285.205 | -109795.4333 | -104567.0794 | -99587.6946 | -94845.4235 | -90328.9747 | -86027.595 | -81931.0428 | -78029.5646 | -74313.871 | -70775.1153 | -67404.8717 | -64195.1159 | -61138.2056 | -58226.8625 | -55454.1548 | -52813.4807 | -50298.5531 | -47903.3839 | -45622.2704 | -43449.7813 | -41380.7441 | -39410.2325 | -37533.5547 | -35746.2426 | -34044.0406 | -32422.8958 | -30878.9484 | -29408.5222
|  | Both | Both | Building | All | Graywater | Materials | Water | Avoided Utility Costs | Reduction in collective wastewater cost for building | -75822.1925 | $/yr | Annual |  |  |  | -1223851.5882 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -75822.1925 | -72211.6119 | -68772.9637 | -65498.0607 | -62379.1054 | -59408.6718 | -56579.6875 | -53885.4166 | -51319.4444 | -48875.6613 | -46548.2489 | -44331.6656 | -42220.6339 | -40210.1275 | -38295.3596 | -36471.771 | -34735.02 | -33080.9714 | -31505.6871 | -30005.4163 | -28576.5869 | -27215.7971 | -25919.8067 | -24685.5302 | -23510.0288 | -22390.5036 | -21324.2891 | -20308.8468 | -19341.7589 | -18420.7227
|  | Both | Both | District | All | Mixed WW | Materials | Water | Avoided Utility Costs | Reduction in collective wastewater cost for building | -243429.1444 | $/yr | Annual |  |  |  | -3929207.7306 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -243429.1444 | -231837.2804 | -220797.4099 | -210283.2475 | -200269.7595 | -190733.1043 | -181650.5755 | -173000.5481 | -164762.4268 | -156916.5969 | -149444.378 | -142327.9791 | -135550.4563 | -129095.6726 | -122948.2597 | -117093.5806 | -111517.6958 | -106207.3294 | -101149.8375 | -96333.1786 | -91745.8843 | -87377.0327 | -83216.2216 | -79253.5444 | -75479.5661 | -71885.301 | -68462.1915 | -65202.0871 | -62097.2258 | -59140.2151
|  | Both | Both | District | All | Graywater | Materials | Water | Avoided Utility Costs | Reduction in collective wastewater cost for building | -150314.1711 | $/yr | Annual |  |  |  | -2426232.0959 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -150314.1711 | -143156.3535 | -136339.3842 | -129847.0326 | -123663.8406 | -117775.0863 | -112166.7488 | -106825.4751 | -101738.5477 | -96893.8549 | -92279.8618 | -87885.5827 | -83700.555 | -79714.8143 | -75918.8707 | -72303.6864 | -68860.6537 | -65581.575 | -62458.6428 | -59484.4217 | -56651.8302 | -53954.124 | -51384.88 | -48937.981 | -46607.6009 | -44388.1914 | -42274.468 | -40261.3981 | -38344.1886 | -36518.2749
|  | Both | Sewered | District | AeMBR | Mixed WW | Materials | Materials | Dewatering | Sludge Disposal | 38676.6577 | $/yr | Annual |  |  |  | 624282.7779 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 38676.6577 | 36834.9121 | 35080.8687 | 33410.3511 | 31819.382 | 30304.1733 | 28861.1175 | 27486.7785 | 26177.8843 | 24931.3184 | 23744.1128 | 22613.4407 | 21536.6102 | 20511.0574 | 19534.3403 | 18604.1337 | 17718.2225 | 16874.4976 | 16070.9501 | 15305.6668 | 14576.8255 | 13882.691 | 13221.6105 | 12592.01 | 11992.3904 | 11421.3242 | 10877.4516 | 10359.4778 | 9866.1693 | 9396.3517
|  | Both | Sewered | District | AeMBR | Graywater | Materials | Materials | Dewatering | Sludge Disposal | 11892.3079 | $/yr | Annual |  |  |  | 191954.6164 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11892.3079 | 11326.0075 | 10786.6738 | 10273.0227 | 9783.8311 | 9317.9344 | 8874.2232 | 8451.6412 | 8049.1821 | 7665.8877 | 7300.8454 | 6953.1861 | 6622.082 | 6306.7448 | 6006.4236 | 5720.4034 | 5448.0033 | 5188.5745 | 4941.4996 | 4706.1901 | 4482.0858 | 4268.6531 | 4065.3839 | 3871.7942 | 3687.4231 | 3511.8315 | 3344.6014 | 3185.3347 | 3033.6521 | 2889.1924
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Equipment
Equalization Aeration and Mixing
| Cost of 50HP Aerator in 1977 | 13960 | $
| Cost of 50HP Aerator in 2016 | 55287.1287 | $
| Treatment System | Required HP | Specified HP | Number | Total Cost
| RVFW, GW | 0.5225 | 0.75 | 2 | 38250.5109
| RVFW, WW | 0.8164 | 1 | 2 | 40433.7165
| Building, MBR WW | 0.39 | 0.5 | 2 | 35419.7746
| Building, MBR GW | 0.25 | 0.35 | 2 | 33146.5444
| District GW | 0.49 | 0.61 | 2 | 36773.6231
| District WW | 0.78 | 1 | 2 | 40433.7165
| Aerator Size | Aerator cost |  | Equipment Cost | Installation Labor
| HP | COSTA | COSTR | Electrical/Mechanical | Labor Hours | Labor Cost
| 0.25 | 7886.4412 | 14.2645 | 5691.1253 | 40.1583 | 2007.9125
| 0.35 | 8632.3901 | 15.6137 | 5929.8046 | 40.2216 | 2011.0775
| 0.5 | 9500.3089 | 17.1836 | 6193.7534 | 40.3165 | 2015.825
| 0.61 | 10021.5287 | 18.1263 | 6345.9763 | 40.3861 | 2019.3065
| 0.75 | 10593.4114 | 19.1607 | 6508.1066 | 40.4748 | 2023.7375
| 1 | 11444.4356 | 20.7 | 6740.7726 | 40.633 | 2031.65
| 5 | 17633.4676 | 31.8943 | 8204.5339 | 43.165 | 2158.25
| 10 | 21241.95 | 38.4211 | 8929.1409 | 46.33 | 2316.5
| 20 | 25588.8659 | 46.2836 | 9717.7437 | 52.66 | 2633
| 50 | 49655.7815 | 89.8144 | 16488.6846 | 71.65 | 3582.5
| *cost calculation from Harris et al. Section… | 2.33.8.8.5 |  | 2.33.9.8.6.3 | 2.33.9.8.6.1 | 2.33.9.8.6.2
Fine Screening Cost
Capital Cost, Screening
| Scenario | Number of Screens | Total Cost
| RVFW, Building GW | 2 | 53481.0516
| RVFW, Building WW | 2 | 70633.0501
| MBR, Building GW | 2 | 24068.9192
| MBR, Building WW | 2 | 31788.103
| District GW | 2 | 36349.1574
| District WW | 2 | 48966.2232
| Qavg | Cost
| 0.01 | 8978.3929
| 0.016 | 12034.4596 | Building GW
| 0.025 | 15894.0515 | Building WW
| 0.031 | 18174.5787 | District GW
| 0.05 | 24483.1116 | District WW
| 0.0576 | 26740.5258 | RVFW GW
| 0.09 | 35316.5251 | RVFW WW
| 0.1 | 37713.6537
| 1 | 158415.8416
| 10 | 665424.2272
| 100 | 2795108.1007
Total bare construction cost calc from Harris et al. 1982 Section 2.47.11.1, in 2016 dollars
*Bare Construction Costs Include Installation. Direct and indirect costs are applied in addition to TBCC.
Chlorination Equipment
| Equipment Cost | 2700 | in 1977 $s
| Equipment Cost | 10693.0693 | in 2016 $s
| Total equipment cost | 46300.9901 | $
| Annual maintenance cost, mechanical equipment | 2315.0495 | $
*Applies to all systems
*Cost calculations from Harris et al. 1982 Sections 3.5.9.7.1 through 3.5.9.7.4
Aeration System Maintenance (Material and Supply Cost)
Percent of bare construction cost
| Q | Cost
| 0.01 | 11.83%
Building GW | 0.016 | 10.47%
Building WW | 0.025 | 9.322%
District GW | 0.031 | 8.815%
District WW | 0.05 | 7.784%
| 0.1 | 6.499%
| 1 | 3.57%
| 10 | 1.961%
| 100 | 1.077%
Cost factor calculation from Harris et al. 1982 Section 2.1.9.5.15
Cost of air piping
|  | Blower Requirement (cfm) | Specified Blower | Cost for 3 trains
|  | 0.5 | 0.575 | 2353.769
|  |  | 1.4217 | 2674.0833
|  | 5.45 | 6.2675 | 4331.3055
| Building AeMBR GW | 26.898 | 30.9327 | 6510.6496
| District GW | 50 | 57.5 | 7627.1772
|  | 55 | 63.25 | 7815.0433
| Building AeMBR WW | 64.8024 | 74.5228 | 8149.2196
|  | 69.4522 | 79.8701 | 8294.6736
|  |  | 100 | 8784.5725
| District WW | 103.156 | 118.6294 | 9176.1797
|  |  | 300 | 11628.6605
|  |  | 600 | 13879.7821
|  |  | 1000 | 15813.2317
|  |  | 10000 | 28465.6191
Cost of air piping from Harris et al. 1982 Section 2.1.9.8.9, in 2016 dollars
|  | Parametric cost factor | 1.8001
Blower
| Cost of 3000 scfm blower | 58808.6185 | $ (in 2016)
| Blower Requirement (cfm) | Specified Blower | COSTRO | Blower Cost | Installed Cost
Building AeMBR GW | 26.898 | 30.9327 | 5.8148 | 3419.6198 | 6839.2396
Building AeMBR WW | 64.8024 | 74.5228 | 10.0026 | 5882.3941 | 11764.7881
District GW | 50 | 57.5 | 8.5239 | 5012.7738 | 10025.5477
District WW | 103.156 | 118.6294 | 13.325 | 7836.2485 | 15672.497
Building AnMBR GW | 44.5602 | 51.2443 | 7.9392 | 4668.9494 | 9337.8987
Building AnMBR WW | 69.6254 | 80.0692 | 10.4555 | 6148.7486 | 12297.4972
Building DHS GW | 0.7912 | 0.90988 | 0.66038 | 388.3606 | 776.7211
Building DHS WW | 1.2362 | 1.4217 | 0.86968 | 511.4494 | 1022.8989
https://www.grainger.com/category/positive-displacement-blowers/blowers/air-compressors-vacuum-pumps-and-blowers/pneumatics/ecatalog/N-1a7n#nav=%2Fcategory%2Fpositive-displacement-blowers%2Fblowers%2Fair-compressors-vacuum-pumps-and-blowers%2Fpneumatics%2Fecatalog%2FN-1a7nZ1z0mn7h
Blower cost calculation from Harris et al. 1982 Section 2.3.7
| Swing arm diffuser cost | 16223.0672 | $ in 2016
| Swing arm count | Diffuser cost | Installation Hours | Installation Cost
Building GW | 3 | 48669.2015 | 75 | 3750
Building WW | 3 | 48669.2015 | 75 | 3750
District GW | 3 | 48669.2015 | 75 | 3750
District WW | 3 | 48669.2015 | 75 | 3750
Pump Cost
| Cost of 3000gpm pump | 20785.8048 | $ (in 2016)
| Installation Cost Factor | 2.5
Permeate Pumping - Cost per Pump (AnMBR and AeMBR)
| Q | GPM | Design Size (GPM) | COSTRO | Pump Cost | Total Pump Cost
Building GW | 0.016 | 11.1111 | 5.5556 | 6.2351 | 1296.0222 | 3240.0556
Building WW | 0.025 | 17.3611 | 8.6806 | 7.5893 | 1577.5052 | 3943.7629
District GW | 0.031 | 21.5278 | 10.7639 | 8.3435 | 1734.258 | 4335.645
District WW | 0.05 | 34.7222 | 17.3611 | 10.2986 | 2140.6438 | 5351.6095
RVFW* |  | 396.2581 | 396.2581 | 40.8218 | 8485.1481 | 21212.8702
* Same for both systems on a per bed basis.
Pump cost calculation from Harris et al. 1982 Section 3.15.4.8.3
Sludge Pumping - Cost per Pump
| Sludge Production (gpm) | Sludge (m3/day)
| RVFW, GW | 0.44288
| RVFW, WW | 1.6196
| Building, AeMBR WW | 1.3333
| Building, AeMBR GW | 0.50384
| Building, AnMBR WW | 0.63
| Building, AnMBR GW | 0.43939
| District GW | 0.9759
| District WW | 2.6265
| System | GPM | Design Size (GPM) | COSTRO | Pump Cost | Total Pump Cost
| RVFW, GW | 0.97496 | 0.48748 | 2.1352 | 443.8248 | 1109.562
| RVFW, WW | 3.5654 | 1.7827 | 3.7796 | 785.6106 | 1964.0266
| Building, AeMBR WW | 2.9351 | 1.4676 | 3.4693 | 721.1144 | 1802.786
| Building, AeMBR GW | 1.1092 | 0.55458 | 2.26 | 469.761 | 1174.4026
| Building, AnMBR WW | 1.3869 | 0.69345 | 2.4937 | 518.3439 | 1295.8597
| Building, AnMBR GW | 0.96728 | 0.48364 | 2.1278 | 442.281 | 1105.7024
| District GW | 2.1484 | 1.0742 | 3.0238 | 628.5251 | 1571.3127
| District WW | 5.782 | 2.891 | 4.6764 | 972.0331 | 2430.0827
Pump cost calculation from Harris et al. 1982 Section 3.15.4.8.3
Anaerobic Reactor Floating Cover
| Cost of 70' Diameter Floating Cover | 281188.1188 | $ (in 2016)
|  | Diameter (Ft) | CAPDET Cost Factor (FLOCOR) | CAPDET Approach | Straight Line
|  | 0 | 0.14 | 39366.3366 | 0
|  | 3 | 0.15231 | 42827.7247 | 9143.7639
|  | 5 | 0.16111 | 45302.7955 | 15239.6064
|  | 10 | 0.18541 | 52134.4747 | 30479.2129
| AnMBR GW | 11.5501 | 0.19366 | 54454.7316 | 35203.6457
| AnMBR Mixed WW | 13.2546 | 0.20316 | 57125.6347 | 40398.9567
|  | 15 | 0.21337 | 59996.3738 | 45718.8193
|  | 20 | 0.24554 | 69043.8503 | 60958.4258
|  | 30 | 0.32518 | 91437.6386 | 91437.6386
|  | 55 | 0.65634 | 184554.6542
|  | 69 | 0.97259 | 273479.6415
|  | 70 | 1.0003 | 281271.029
CAPDET Approach is intended for tanks with a diameter of between 30 and 70 feet.
The straight line approach is used to estimate floating cover cost for tanks with a diameter of <30 ft.
Cost of Gas Safety Equipment
| Purchase price of gas safety equipment | 28118.8119
| GPS Size (in) | 2
| GPS | CGSER
| 2 | 1 | Both AnMBRs
| 3 | 1.1625
| 4 | 1.325
| 6 | 1.65
| Safety Equipment Cost | 28118.8119 | 2016 $
| Installation Cost | 25306.9307 | 2016 $
Zeolite Equipment Cost
Uses activated carbon system as a proxy.
Costs are adjusted from 1977 to 2016 $s.
Adsorber Cost
| Qp | Cost | $/MGD
| 0.005 | 23490.1425 | 4698028.4965
| 0.016 | 46495.2608 | 2905953.8016 | AnMBR GW
| 0.025 | 60420.0449 | 2416801.7956 | AnMBR Mixed WW
| 0.05 | 90758.1534 | 1815163.0683
| 0.5 | 350659.5338 | 701319.0676
| 1 | 526732.6733 | 526732.6733
| 5 | 1354832.6404 | 270966.5281
| 10 | 2035121.1069 | 203512.1107
Cost calculations from Harris et al. 1982 Section 2.5.8
|  | Parametric cost increase | 3.8637
Feed System Cost
| Qp | Cost | $/MGD
| 0.005 | 5852.6018 | 1170520.351
| 0.016 | 11760.8567 | 735053.5469 | AnMBR GW
| 0.025 | 15372.0212 | 614880.8495 | AnMBR Mixed WW
| 0.05 | 23299.6273 | 465992.545
| 0.5 | 92757.4868 | 185514.9736
| 1 | 140594.0594 | 140594.0594
| 5 | 369274.2062 | 73854.8412
| 10 | 559715.0319 | 55971.5032
Cost calculations from Harris et al. 1982 Section 2.5.8
|  | Parametric cost increase | 3.9811
Backwash - Used to estimate NaCl Regeneration Costs
| Qp | Cost | $/MGD
| 0.005 | 15866.0374 | 3173207.4817
| 0.016 | 24684.5643 | 1542785.2675
| 0.025 | 29246.7138 | 1169868.5528
| 0.05 | 38059.9728 | 761199.4566
| 0.5 | 91299.5157 | 182599.0314
| 1 | 118811.8812 | 118811.8812
| 1.5 | 138603.6128 | 92402.4086
| 3 | 180370.6827 | 60123.5609
| 5 | 219012.2838 | 43802.4568
| 10 | 285009.8518 | 28500.9852
|  | Parametric cost increase | 2.3988
For every tripling of flowrate, cost increases by 50%
1.5181
NaCl Regeneration flowrate is ~1/3 of backwash flowrate. Assume 1/2 as a conservative estimate.
Therefore decrease system costs by 30%.
| 0.016 | 16259.9569 | AnMBR GW
| 0.025 | 19265.0881 | AnMBR Mixed WW
Carbon Handling System - Used to estimate zeolite replacement system costs
| Qp | Cost | $/MGD
| 0.005 | 17607.8484 | 3521569.6779
| 0.016 | 24386.4332 | 1524152.074 | AnMBR GW
| 0.025 | 27632.3545 | 1105294.1786 | AnMBR Mixed WW
| 0.05 | 33551.0634 | 671021.2687
| 0.5 | 63930.2334 | 127860.4668
| 1 | 77623.7624 | 77623.7624
| 5 | 121816.5485 | 24363.3097
| 10 | 147909.03 | 14790.903
*for every order of magnitude increase in flowrate system cost increases by 190%.
|  | Parametric cost increase | 1.9055
Heat Pump
| Heat Pump Size | Minimum Size | Design Size | Units
| District GW | 18.5997 | 21.5 | kW
| District WW | 28.6103 | 31 | kW
| Parameter | Value | Units | Source
| 2014 Euro to US Dollar Conversion | 0.784 |  | IRS 2018
| Cost of 22 kW Unit | 10666 | Euros 2014 | PZP 2014
| Cost of 31 kW Unit | 13536 | Euros 2014 | PZP 2014
| Cost of 22 kW Unit | 13794.263 | 2016 $s
| Cost of 31 kW Unit | 17506.0138 | 2016 $s
| Total Cost Factor | 2.5
Graywater | Installed Cost of 22 kW Unit | 34485.6574 | 2016 $s
Mixed Wastewater | Installed Cost of 31 kW Unit | 43765.0345 | 2016 $s
| 22kW Direct Cost | 15518.5458 | 2016 $s
| 31kW Direct Cost | 19694.2655 | 2016 $s
| 22kW Indirect Cost | 25502.1436 | 2016 $s
| 31kW Indirect Cost | 32364.243 | 2016 $s
Avoided Utility Costs
Avoided Potable Water Cost
| 2016 Residential Water Rate | -5.58 | 2016 $ per ccf
| 2016 Commercial Water Rate | -6.49 | 206 $ per ccf
|  |  | Scale Scenario | Residential Reuse Volume (MGY) | Commercial Reuse Volume (MGY) | Total Reuse Volume (MGY) | Residential Reuse Volume (ccf, =748 gallons) | Commercial Reuse Volume (ccf, =748 gallons) | Annual reduction in potable water bill for building/district
| Low Reuse Scenario | Mixed WW | Building | 2.1 | 1.08 | 3.18 | 2807.4866 | 1443.8503 | -25036.3636
| High Reuse Scenario | Mixed WW | Building | 4.3 | 2.2 | 6.5 | 5748.6631 | 2941.1765 | -51165.7754
| Low Reuse Scenario | GW | Building | 2.1 | 1.08 | 3.18 | 2807.4866 | 1443.8503 | -25036.3636
| High Reuse Scenario | GW | Building | 4.3 | 2.2 | 6.5 | 5748.6631 | 2941.1765 | -51165.7754
| Low Reuse Scenario | Mixed WW | District | 4.6 | 1.75 | 6.35 | 6149.7326 | 2339.5722 | -49499.3316
| High Reuse Scenario | Mixed WW | District | 8.4 | 4.8 | 13.2 | 11229.9465 | 6417.1123 | -104310.1604
| Low Reuse Scenario | GW | District | 4.6 | 1.75 | 6.35 | 6149.7326 | 2339.5722 | -49499.3316
| High Reuse Scenario | GW | District | 8.4 | 4.8 | 13.2 | 11229.9465 | 6417.1123 | -104310.1604
Avoided Wastewater Fees
| WW Rate | -9.95 | 2016 $ per ccf
|  |  | Scale Scenario | WW Treated (MGY) | WW Treated (ccf) | Annual reduction in wastewater treatment bill for building/district
| Low Reuse Scenario | Mixed WW | Building | 9.1 | 12165.7754 | -121049.4652
| High Reuse Scenario | Mixed WW | Building | 9.1 | 12165.7754 | -121049.4652
| Low Reuse Scenario | GW | Building | 5.7 | 7620.3209 | -75822.1925
| High Reuse Scenario | GW | Building | 5.7 | 7620.3209 | -75822.1925
| Low Reuse Scenario | Mixed WW | District | 18.3 | 24465.2406 | -243429.1444
| High Reuse Scenario | Mixed WW | District | 18.3 | 24465.2406 | -243429.1444
| Low Reuse Scenario | GW | District | 11.3 | 15106.9519 | -150314.1711
| High Reuse Scenario | GW | District | 11.3 | 15106.9519 | -150314.1711
Cost of Solids Disposal in the Sanitary Sewer
| 2016 Non-residential sewer discharge fee | 6.453 | 2016 $ per ccf
| TSS fee | 0.87 | $ per pound
| COD fee | 0.462 | $ per pound
| District Sewered Scenario - Mixed Wastewater | Quantity |  | Cost (2016 $)
| District WAS generation (volume to sewer) | 338.5809 | ccf per year | 2184.8627
| WAS TSS content | 25485.4753 | pounds per year | 22172.3635
| WAS COD content | 30994.4405 | pounds per year | 14319.4315
| District Sewered Scenario - Graywater |  |  | Cost (2016 $)
| District WAS generation (volume to sewer) | 125.8009 | ccf per year | 811.793
| WAS TSS content | 8259.3707 | pounds per year | 7185.6525
| WAS COD content | 8430.438 | pounds per year | 3894.8624
cost factors from SFWPS 2017

## ResultsExport (hidden)
LCCA Results
| Treatment System | Wastewater Type | System Scale | Reuse Scenario | Sewered/Unsewered | Process Category | Process | Interest During Construction | Capital | O&M Labor ($) | Material ($) | Chemical ($) | Energy ($)
| RVFW | Graywater | Building | Low Reuse | Sewered | Preliminary/Primary | Thermal Recovery | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Preliminary/Primary | Equalization | 2969.7685 | 116461.5109 | 34487.6722 | 53806.7794 | 0 | 16444.7623
| RVFW | Graywater | Building | Low Reuse | Sewered | Preliminary/Primary | Clarification | 2764.761 | 108422 | 282468.7876 | 13930.9845 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Preliminary/Primary | Fine Screen | 2985.9748 | 117097.0516 | 184428.7216 | 70173.6447 | 0 | 7911.8809
| RVFW | Graywater | Building | Low Reuse | Sewered | Biological Treatment | Wetland | 14378.736 | 563872 | 0 | 328735.5161 | 0 | 31378.983
| RVFW | Graywater | Building | Low Reuse | Sewered | Biological Treatment | AeMBR | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Biological Treatment | AnMBR | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Sludge Handling and Disposal | Dewatering | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Sludge Handling and Disposal | Composting | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Post-Treatment | Zeolite | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Post-Treatment | DHS | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Disinfection | Ozone | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Disinfection | UV | 579.768 | 22736 | 19369.2883 | 8922.9057 | 0 | 4118.7433
| RVFW | Graywater | Building | Low Reuse | Sewered | Disinfection | Chlorination | 2723.2212 | 106792.9901 | 13547.8749 | 73863.9201 | 1087.7991 | 6001.8851
| RVFW | Graywater | Building | Low Reuse | Sewered | Building Reuse | Building Reuse | 25733.3135 | 1009149.5501 | 0 | 189227.1234 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Other | Administration | 0 | 0 | 1262276.9616 | 0 | 0 | 0
| RVFW | Graywater | Building | Low Reuse | Sewered | Total | Total | 52135.5431 | 2044531.1027 | 1796579.3062 | 738660.874 | 1087.7991 | 65856.2546
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Preliminary/Primary | Thermal Recovery | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Preliminary/Primary | Equalization | 3337.9683 | 130900.7165 | 37317.6105 | 57739.3849 | 0 | 21929.7065
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Preliminary/Primary | Clarification | 4180.5975 | 163945 | 282468.7876 | 21566.1912 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Preliminary/Primary | Fine Screen | 3943.6018 | 154651.0501 | 214475.8949 | 92679.153 | 0 | 9731.2443
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Biological Treatment | Wetland | 21568.1295 | 845809 | 0 | 493107.6481 | 0 | 47070.3439
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Biological Treatment | AeMBR | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Biological Treatment | AnMBR | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Sludge Handling and Disposal | Dewatering | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Sludge Handling and Disposal | Composting | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Post-Treatment | Zeolite | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Post-Treatment | DHS | 0 | 0 | 0 | 0 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Disinfection | Ozone | 4079.745 | 159990 | 453620.6614 | 110066.1456 | 0 | 24319.7189
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Disinfection | UV | 579.768 | 22736 | 19369.2883 | 8922.9057 | 0 | 4118.7433
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Disinfection | Chlorination | 2772.6657 | 108731.9901 | 17617.3012 | 75951.6334 | 1786.747 | 6001.8851
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Building Reuse | Building Reuse | 13969.046 | 547805.7248 | 0 | 114316.1588 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Other | Administration | 0 | 0 | 1370313.5636 | 0 | 0 | 0
| RVFW | Mixed WW | Building | Low Reuse | Sewered | Total | Total | 54431.5218 | 2134569.4815 | 2395183.1075 | 974349.2207 | 1786.747 | 113171.6419
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Preliminary/Primary | Thermal Recovery | 2443.5003 | 95823.5431 | 0 | 57425.0485 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Preliminary/Primary | Equalization | 2822.3088 | 110678.7746 | 32248.8761 | 50138.2691 | 0 | 11251.8561
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Preliminary/Primary | Clarification | 0 | 0 | 0 | 0 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Preliminary/Primary | Fine Screen | 1774.8026 | 69600.103 | 128962.0762 | 41709.8576 | 0 | 9731.2443
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Biological Treatment | Wetland | 0 | 0 | 0 | 0 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Biological Treatment | AeMBR | 10404.3876 | 408015.2015 | 278921.3299 | 386951.3828 | 817.0799 | 72170.3183
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Biological Treatment | AnMBR | 0 | 0 | 0 | 0 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Sludge Handling and Disposal | Dewatering | 0 | 0 | 0 | 0 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Sludge Handling and Disposal | Composting | 0 | 0 | 0 | 0 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Post-Treatment | Zeolite | 0 | 0 | 0 | 0 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Post-Treatment | DHS | 0 | 0 | 0 | 0 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Disinfection | Ozone | 0 | 0 | 0 | 0 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Disinfection | UV | 282.744 | 11088 | 19369.2883 | 3596.2214 | 0 | 1587.747
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Disinfection | Chlorination | 2772.6657 | 108731.9901 | 27340.3461 | 78579.8991 | 4085.3994 | 6001.8851
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Building Reuse | Building Reuse | 13969.046 | 547805.7248 | 0 | 114316.1588 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Other | Administration | 0 | 0 | 1370313.5636 | 0 | 0 | 0
| AeMBR | Mixed WW | Building | Low Reuse | Sewered | Total | Total | 34469.4551 | 1351743.3372 | 1857155.4802 | 732716.8373 | 4902.4793 | 100743.0508

## Labor
Plant Labor Requirements
Adminstrative Labor
| Q (MGD) | AMH (hrs/yr) | Administrative Labor Rate
| 0.01 | 9.4766 | 508.1903
| 0.016 | 13.6917 | 451.5739 | Building GW
| 0.02 | 16.3053 | 426.9473
| 0.025 | 19.4178 | 403.6637 | Building WW
| 0.031 | 22.9794 | 382.4211 | District GW
| 0.05 | 33.4099 | 339.1311 | District WW
| 0.25 | 117.7875 | 226.3127
| 1 | 348.7 | 159.7367
| 5 | 1229.3501 | 106.5972
| 10 | 2115.2025 | 89.5558
| 100 | 12830.7472 | 50.2091
Labor rate calculations from Harris et al. 1982 Page 1.2-13
Loaded Labor Rate
| 50 | $/hour
Annual Adminstrative Labor Cost
| Building GW | 6182.8159 | $/yr
| Building WW | 7838.2467 | $/yr
| District GW | 8787.8144 | $/yr
| District WW | 11330.3465 | $/yr
Laboratory Labor
| Q (MGD) | AMH (hrs/yr)
| 0.01 | 1219.4559
| 0.016 | 1309.454 | Building GW
| 0.02 | 1354.4785
| 0.025 | 1401.0512 | Building WW
| 0.031 | 1447.4627 | District GW
| 0.05 | 1556.1808 | District WW
| 0.25 | 1985.8845
| 1 | 2450
| 5 | 3126.5116
| 10 | 3472.6905
| 100 | 8153.1328
Labor rate calculations from Harris et al. 1982 Page 1.2-13 through 1.2-14
Laboratory Labor Rate
| 55 | $/hour
Laboratory Labor Cost
| Building GW | 72019.9725 | $/yr
| Building WW | 77057.8141 | $/yr
| District GW | 79610.4485 | $/yr
| District WW | 85589.9415 | $/yr
Chlorine and Ozone Operational Labor Requirements
| Chlorine Requirement (lb/day) | OMH (hr/yr) |  |  |  |  | Chlorine Requirement (lb/day) | MH (hr/year)
| 0.1 | 11.9026 |  |  |  |  | 0.1 | 7.6755
| 0.5 | 28.0035 |  |  |  |  | 0.5 | 12.7249
| 1 | 40.48 |  |  |  |  | 1 | 15.82
| 2.8027 | 70.0125 |  |  |  |  | 2.8027 | 21.8672
| 10 | 137.6704 |  |  |  |  | 10 | 32.6067
| 20 | 199.0069 |  |  |  |  | 20 | 40.5378
| 50 | 323.9015 |  |  |  |  | 50 | 54.0571
Chlorine Operational and Maintenance Labor Requirement
| Building GW - AeMBR | 0.40726 | lb Cl/day
| Building WW - AeMBR | 0.71535 | lb Cl/day
| Building GW - AnMBR | 0.73608 | lb Cl/day
| Building WW - AnMBR | 2.4688 | lb Cl/day
| Building GW - RVFW | 0.19094 | lb Cl/day
| Building WW - RVFW | 0.31295 | lb Cl/day
| District GW - AeMBR | 0.79566 | lb Cl/day
| District WW - AeMBR | 1.4502 | lb Cl/day
Operations | Building GW - AeMBR | 1255.4977 | $/yr
Operations | Building WW - AeMBR | 1693.8369 | $/yr
Operations | Building GW - AnMBR | 1719.7565 | $/yr
Operations | Building WW - AnMBR | 3272.3053 | $/yr
Operations | Building GW - RVFW | 839.3416 | $/yr
Operations | Building WW - RVFW | 1091.4578 | $/yr
Operations | District GW - AeMBR | 1792.4049 | $/yr
Operations | District WW - AeMBR | 2466.2081 | $/yr
Maintenance | Building GW - AeMBR | 596.5348 | $/yr
Maintenance | Building WW - AeMBR | 712.0003 | $/yr
Maintenance | Building GW - AnMBR | 718.4178 | $/yr
Maintenance | Building WW - AnMBR | 1050.6426 | $/yr
Maintenance | Building GW - RVFW | 470.2277 | $/yr
Maintenance | Building WW - RVFW | 549.1694 | $/yr
Maintenance | District GW - AeMBR | 736.1975 | $/yr
Maintenance | District WW - AeMBR | 888.9625 | $/yr
OMMP | Building GW - AeMBR | 6.7193 | %
OMMP | Building WW - AeMBR | 6.4242 | %
OMMP | Building GW - AnMBR | 6.4096 | %
OMMP | Building WW - AnMBR | 5.8203 | %
OMMP | Building GW - RVFW | 7.1374 | %
OMMP | Building WW - RVFW | 6.8618 | %
OMMP | District GW - AeMBR | 6.37 | %
OMMP | District WW - AeMBR | 6.0724 | %
|  | 6.4769 | All Systems
O&M Labor calculation from Harris et al. 1982 Section 3.5.6.7
OMMP cost factor calculation from Harris et al. 1982 Section 3.5.6.10
Ozone
Annual labor hours for operation of an ozone generation system are:
| 550 | hours per year for 5-10 lb/day systems (Hansen et al. 1979)
| Cost per year | 27500 | $/yr | All Systems
UV Operations Labor
Labor hour requirement for a 10-130 GPM UV treatment system
| 24 | hours per year | Hansen et al. 1979
| Cost per year | 1200 | $/year (2016 dollars) | All Systems
Fine Screen Labor Requirements
| Q (MGD) | AMH (hrs/yr)
| 0.01 | 126.4012
| 0.016 | 148.1783 | Building GW
| 0.02 | 159.7937
| 0.025 | 172.3196 | Building WW
| 0.031 | 185.3232 | District GW
| 0.05 | 217.8426 | District WW
| 0.0576 | 228.521 | Bulding GW, RVFW
| 0.09 | 265.7517 | Building WW, RVFW
| 0.25 | 375.4348
| 1 | 600
| 3 | 869.9888
Labor hour requirement calculation from Harris et al. 1982 Section 2.47.8.1
Fine screen operation labor cost
| Building GW | 7408.9154 | $/yr
| Building WW | 7989.6839 | $/yr
| District GW | 8615.9777 | $/yr
| District WW | 9266.1597 | $/yr
| Bulding GW, RVFW | 11426.0505 | $/yr
| Building WW, RVFW | 13287.5855 | $/yr
CSTR AeMBR and AnMBR
Operations and Maintenance
Estimated Airflow
| Building GW, AeMBR | 30.9327 | scfm
| Building WW, AeMBR | 74.5228 | scfm
| District GW | 57.5 | scfm
| District WW | 118.6294 | scfm
| Building GW, AnMBR | 51.2443 | scfm
| Building WW, AnMBR | 80.0692 | scfm
(hours/year)
| Treatment System | Operational Labor | Maintenance
| Building GW | 243.725 | 102.558
| Building WW | 345.6044 | 150.727
| District GW | 311.7785 | 134.5471
| District WW | 415.6954 | 184.7585
| Building GW, AnMBR | 297.836 | 127.9291
| Building WW, AnMBR | 355.6006 | 155.5404
Operations labor requirement calculation from Harris et al. 1982 Section 2.1.9.5.12
Maintenance labor requirement calculation from Harris et al. 1982 Section 2.1.9.5.13
Floating Cover Installation Labor Hours
|  | Diameter | IMH
| AnMBR Mixed WW | 11.5501 | 45.9104
| AnMBR GW | 13.2546 | 60.1789
| Diameter | IMH
| 1 | 0.374
| 5 | 8.8521
| 15 | 76.748
| 30 | 299.8417
| 55 | 987.2443
| 70 | 1586.1138
| 100 | 3197.9495
Installation labor requirement calculation from Harris et al. 1982 Section 2.19.6.8.5.4
Zeolite System
| O&M Hours | 150.2187 | hours
| Labor Cost | 7510.9363 | $/yr
| Qavg | Cost | hr/MGD
| 0.005 | 70.1635 | 14032.7006
| 0.016 | 121.6318 | 7601.9887 | AnMBR GW
| 0.025 | 150.2187 | 6008.7491 | AnMBR Mixed WW
| 0.05 | 208.5025 | 4170.05
| 0.5 | 619.5998 | 1239.1996
| 1 | 860 | 860
| 5 | 1841.2437 | 368.2487
| 10 | 2555.6328 | 255.5633
Zeolite O&M hour requirement calculation from Harris et al. 1982 Section 2.5.5.6
|  | Parametric Labor Factor | 2.9717
maintenance and material costs
| Qavg | Cost | %/MGD
| 0.005 | 2.0779 | 415.5768
| 0.016 | 1.7425 | 108.904 | AnMBR GW
| 0.025 | 1.6138 | 64.5507 | AnMBR Mixed WW
| 0.05 | 1.4139 | 28.2777
| 0.5 | 0.74988 | 1.4998
| 1 | 0.55 | 0.55
| 4 | 0.15023 | 0.037558
Maintenance materials cost factor calculation from Harris et al. 1982 Section 2.5.5.6.3
DHS System
Operation Labor Hours
| Qavg | hr/yr | cost
| 0.005 | 25.9777 | 1298.8827
| 0.016 | 36.868 | 1843.4021 | Building GW
| 0.025 | 42.1687 | 2108.4335 | Building WW
| 0.05 | 51.9517 | 2597.5861
| 0.5 | 103.8963 | 5194.8133
| 1 | 128 | 6400
| 5 | 207.7782 | 10388.9091
| 10 | 255.9823 | 12799.116
Operations labor requirement calculation from Harris et al. 1982 Section 2.41.8.4.13.1
Maintenance Labor Hours
| Qavg | hr/yr | cost
| 0.005 | 30.9078 | 1545.3887
| 0.016 | 41.0033 | 2050.1667 | Building GW
| 0.025 | 45.7001 | 2285.0065 | Building WW
| 0.05 | 54.0839 | 2704.1933
| 0.5 | 94.6385 | 4731.9238
| 1 | 112 | 5600
| 5 | 165.6028 | 8280.1411
| 10 | 195.9828 | 9799.1415
Maintenance labor requirement calculation from Harris et al. 1982 Section 2.41.8.4.13.2
Clarification
| Capdet costing manual indicates that for clarifiers with a surface area <1000 ft2, that operation manpower = |  |  |  | 350 | hours/year
Screw Press
| Estimated Daily Operator Time | 0.33333 | hours | Macomber 2016
| Annual operator time | 121.75 | hours
| Annual Operator cost | 6087.5 | $/yr

## ResultsFigures
Baseline Report LCCA Results Figures (Static Values Generated from "LCCA" Calculator)
Mixed Wastewater - Building Scale
|  | AeMBR |  | AnMBR |  |  | RVFW |  | AeMBR - Thermal Recovery |  |  | AeMBR |  | AnMBR |  | RVFW |  | AeMBR - Thermal Recovery
|  | Low Reuse | High Reuse | Low Reuse | High Reuse |  | Low Reuse | High Reuse | Low Reuse | High Reuse |  | Low Reuse | High Reuse | Low Reuse | High Reuse | Low Reuse | High Reuse | Low Reuse | High Reuse
| Preliminary/Primary | 458918.1685 | 458918.1685 | 458918.1685 | 458918.1685 |  | 1198866.907 | 1198866.907 | 614610.2605 | 614610.2605 | Interest During Construction | 32025.9547 |  | 53319.2218 |  | 54431.5218 |  | 34469.4551
| Biological Treatment | 1157279.7 | 1157279.7 | 1672721.955 | 1672721.955 |  | 1407555.1215 | 1407555.1215 | 1157279.7 | 1157279.7 | Capital | 1255919.7941 |  | 2090949.8735 |  | 2134569.4815 |  | 1351743.3372
| Post-Treatment | 0 | 0 | 893992.8881 | 893992.8881 |  | 0 | 0 | 0 | 0 | O&M Labor | 2098450.1024 |  | 2349474.8978 |  | 2938238.7799 |  | 2116110.4684
| Disinfection | 263210.2388 | 263210.2388 | 304161.2312 | 304161.2312 |  | 1020086.8336 | 1020086.8336 | 263210.2388 | 263210.2388 | Materials | 433771.2192 |  | 628173.1702 |  | 420974.0453 |  | 473535.9017
| Building Reuse | 676090.9296 | 715712.273 | 676090.9296 | 715712.273 |  | 676090.9296 | 715712.273 | 676090.9296 | 715712.273 | Chemicals | 4902.4793 |  | 126808.3693 |  | 11527.8849 |  | 4902.4793
| Other (b) | 1370313.5636 | 1370313.5636 | 1370313.5636 | 1370313.5636 |  | 1370313.5636 | 1370313.5636 | 1370313.5636 | 1370313.5636 | Energy | 100743.0508 |  | 127474.6917 |  | 113171.6419 |  | 100743.0508
| Total | 3900000 | 4000000 | 5400000 | 5400000 |  | 5700000 | 5700000 | 4100000 | 4100000 | Total | 3900000 |  | 5400000 |  | 5700000 |  | 4100000
Formula for copying from LCCA Calculator
| Formula (Except AeMBR Thermal) | 0 |  |  |  | ` |  |  |  |  | Formula for copying from LCCA Calculator
| AeMBR Thermal | 0 | [8 empty] | Formula (Except AeMBR Thermal) | 0
[11 empty] | AeMBR Thermal | 0
Graywater - Building Scale
|  | AeMBR |  | AnMBR |  |  | RVFW |  | AeMBR - Thermal Recovery |  |  | AeMBR |  | AnMBR |  | RVFW |  | AeMBR - Thermal Recovery
|  | Low Reuse | High Reuse | Low Reuse | High Reuse |  | Low Reuse | High Reuse | Low Reuse | High Reuse |  | Low Reuse | High Reuse | Low Reuse | High Reuse | Low Reuse | High Reuse | Low Reuse | High Reuse
| Preliminary/Primary | 397096.2351 | 397096.2351 | 397096.2351 | 397096.2351 |  | 1014354.3001 | 1014354.3001 | 519777.3708 | 519777.3708 | Interest During Construction | 40882.2913 |  | 54464.2965 |  | 52135.5431 |  | 42807.7032
| Biological Treatment | 885463.1328 | 885463.1328 | 1292439.1198 | 1292439.1198 |  | 938365.2352 | 938365.2352 | 885463.1328 | 885463.1328 | Capital | 1603227.1107 |  | 2135854.7647 |  | 2044531.1027 |  | 1678733.4576
| Post-Treatment | 0 | 0 | 599963.6917 | 599963.6917 |  | 0 | 0 | 0 | 0 | O&M Labor | 1880768.4496 |  | 2115385.4821 |  | 2225968.5914 |  | 1894684.3379
| Disinfection | 246307.0354 | 246307.0354 | 257648.2633 | 257648.2633 |  | 259166.0309 | 259166.0309 | 246307.0354 | 246307.0354 | Materials | 432754.894 |  | 602753.4199 |  | 308693.2238 |  | 464088.3827
| Building Reuse | 1224109.987 | 1262894.8884 | 1224109.987 | 1262894.8884 |  | 1224109.987 | 1262894.8884 | 1224109.987 | 1262894.8884 | Chemicals | 2845.0131 |  | 38860.6265 |  | 1087.7991 |  | 2845.0131
| Other (b) | 1262276.9616 | 1262276.9616 | 1262276.9616 | 1262276.9616 |  | 1262276.9616 | 1262276.9616 | 1262276.9616 | 1262276.9616 | Energy | 54775.5932 |  | 86215.2159 |  | 65856.2546 |  | 54775.5932
| Total | 4000000 | 4100000 | 5000000 | 5100000 |  | 4700000 | 4700000 | 4100000 | 4200000 | Total | 4000000 |  | 5000000 |  | 4700000 |  | 4100000
Mixed Wastewater - District Scale
|  | Sewered |  | Unsewered | [7 empty] | Sewered |  | Unsewered
|  | Low Reuse | High Reuse | Low Reuse | High Reuse | [6 empty] | Low Reuse | High Reuse | Low Reuse | High Reuse
| Preliminary/Primary | 608585.8909 |  | 608585.8909 | [6 empty] | Interest During Construction | 51762.8972 |  | 55500.4393
| Biological Treatment | 1515824.3922 |  | 1625150.253 | [6 empty] | Capital | 2029917.5375 |  | 2176487.8151
| Post-Treatment | 0 |  | 0 | [6 empty] | O&M Labor | 2489180.0956 |  | 2614394.4739
| Disinfection | 302417.0757 |  | 302239.8777 | [6 empty] | Materials | 1227818.92 |  | 1502707.6011
| Building Reuse | 1371199.8398 |  | 1371199.8398 | [6 empty] | Chemicals | 9908.3241 |  | 15291.7259
| Sludge Handling and Disposal | 624282.7779 |  | 1071163.3691 | [6 empty] | Energy | 178119.7022 |  | 178354.6754
| Other (a) | 1564397.5001 |  | 1564397.5001 | [6 empty] | Total | 6000000 |  | 6500000
| Total | 6000000 |  | 6500000
Graywater - District Scale
|  | Sewered | [9 empty] | Sewered
|  | Low Reuse | High Reuse | [8 empty] | Low Reuse | High Reuse
| Preliminary/Primary | 507853.1207 | [8 empty] | Interest During Construction | 70326.6562
| Biological Treatment | 1135161.1919 | [8 empty] | Capital | 2757908.0872
| Post-Treatment | 0 | [8 empty] | O&M Labor | 2265273.7471
| Disinfection | 273252.7141 | [8 empty] | Materials | 796155.3596
| Building Reuse | 2453365.4864 | [8 empty] | Chemicals | 1013.9666
| Sludge Handling and Disposal | 191954.6164 | [8 empty] | Energy | 97752.1785
| Other (a) | 1426842.8657 | [8 empty] | Total | 6000000
| Total | 6000000
a

## Sensitivity Analyses
LCCA - Biogas Sparging Sensitivity (Static Values Generated from "LCCA" Calculator)
|  | Mixed Wastewater |  | Graywater
|  | Continuous Sparging | Intermittent Sparging | Continuous Sparging | Intermittent Sparging
|  | Low Reuse | Low Reuse | Low Reuse | Low Reuse | [6 empty] | High Reuse
| Preliminary/Primary | 458918.1685 | 458918.1685 | 397096.2351 | 397096.2351
| Biological Treatment | 1672721.955 | 1614847.679 | 1292439.1198 | 1254746.9359
| Post-Treatment | 893992.8881 | 893992.8881 | 599963.6917 | 599963.6917
| Disinfection | 304161.2312 | 304161.2312 | 257648.2633 | 257648.2633
| Building Reuse | 676090.9296 | 676090.9296 | 1224109.987 | 1224109.987
| Other (a) | 1370313.5636 | 1370313.5636 | 1262276.9616 | 1262276.9616
| Total | 5400000 | 5300000 | 5000000 | 5000000 | [6 empty] | 0
| Formula (Except AeMBR Thermal) | 0
Mixed Wastewater - Building Scale
|  | AeMBR | AnMBR | RVFW | AeMBR - Thermal Recovery | Avoided Utility Cost | AeMBR | AnMBR | RVFW | AeMBR - Thermal Recovery | Avoided Utility Cost
|  | Low Reuse |  |  |  |  | High Reuse
| Preliminary/Primary | 458918.1685 | 458918.1685 | 1198866.907 | 614610.2605 |  | 458918.1685 | 458918.1685 | 1198866.907 | 614610.2605
| Biological Treatment | 1157279.7 | 1672721.955 | 1407555.1215 | 1157279.7 |  | 1157279.7 | 1672721.955 | 1407555.1215 | 1157279.7
| Post-Treatment | 0 | 893992.8881 | 0 | 0 |  | 0 | 893992.8881 | 0 | 0
| Disinfection | 263210.2388 | 304161.2312 | 1020086.8336 | 263210.2388 |  | 263210.2388 | 304161.2312 | 1020086.8336 | 263210.2388
| Building Reuse | 676090.9296 | 676090.9296 | 676090.9296 | 676090.9296 |  | 715712.273 | 715712.273 | 715712.273 | 715712.273
| Other (b) | 1370313.5636 | 1370313.5636 | 1370313.5636 | 1370313.5636 |  | 1370313.5636 | 1370313.5636 | 1370313.5636 | 1370313.5636
| Avoided Utility Cost |  |  |  |  | -2357982.1126 |  |  |  |  | -2779738.8705
| Total | 3900000 | 5400000 | 5700000 | 4100000 | -2400000 | 4000000 | 5400000 | 5700000 | 4100000 | -2800000
|  | $3.9M | $5.4M | $5.7M | $4.1M | $-2.4M | $4M | $5.4M | $5.7M | $4.1M | $-2.8M
`
Graywater - Building Scale
|  | AeMBR | AnMBR | RVFW | AeMBR - Thermal Recovery | Avoided Utility Cost | AeMBR | AnMBR | RVFW | AeMBR - Thermal Recovery | Avoided Utility Cost
|  | Low Reuse | Low Reuse | Low Reuse | Low Reuse | Low Reuse | High Reuse | High Reuse | High Reuse | High Reuse | High Reuse
| Preliminary/Primary | 397096.2351 | 397096.2351 | 1014354.3001 | 519777.3708 |  | 397096.2351 | 397096.2351 | 1014354.3001 | 519777.3708
| Biological Treatment | 885463.1328 | 1292439.1198 | 938365.2352 | 885463.1328 |  | 885463.1328 | 1292439.1198 | 938365.2352 | 885463.1328
| Post-Treatment | 0 | 599963.6917 | 0 | 0 |  | 0 | 599963.6917 | 0 | 0
| Disinfection | 246307.0354 | 257648.2633 | 259166.0309 | 246307.0354 |  | 246307.0354 | 257648.2633 | 259166.0309 | 246307.0354
| Building Reuse | 1224109.987 | 1224109.987 | 1224109.987 | 1224109.987 |  | 1262894.8884 | 1262894.8884 | 1262894.8884 | 1262894.8884
| Other (b) | 1262276.9616 | 1262276.9616 | 1262276.9616 | 1262276.9616 |  | 1262276.9616 | 1262276.9616 | 1262276.9616 | 1262276.9616
| Avoided Utility Cost |  |  |  |  | -1627965.3758 |  |  |  |  | -2049722.1337
| Total | 4000000 | 5000000 | 4700000 | 4100000 | -1600000 | 4100000 | 5100000 | 4700000 | 4200000 | -2000000
|  | $4M | $5M | $4.7M | $4.1M | $-1.6M | $4.1M | $5.1M | $4.7M | $4.2M | $-2M
a

## Sources
Sources | General Information |  |  | Additional information
No | Name | Description | Category | Doi | Text reference | Year
1 | Atlantic UV 2007 |  |  |  | Atlantic UV Corp. 2007. Sanitron® Ultraviolet Water Purifiers. Hauppauge, NY: Atlantic Ultraviolet Corporation.
2 | Carollo Engineers 2012 |  |  |  | Carollo, E. 2012. Long Range Facilities Plan for the Regional Water Quality Control Plant. City of Palo Alto.
3 | City of Alexandria 2015 |  |  |  | City Of Alexandria. 2015. CSS Long Term Control Plan Update, Basis for Cost Opinions. City of Alexandria, VA.
4 | Gross et al. 2007a |  |  |  | Gross, A., Shmueli, O., Ronen, Z., & E., R. (2007). Recycled vertical flow constructed wetland ( RVFCW )— a novel method of recycling greywater for irrigation in small communities and households. Chemosphere, 66, 916–923. https://doi.org/10.1016/j.chemosphere.2006.06.006
5 | Hansen et al. 1979 |  |  |  | Hansen, S. P., R. C. Gumerman, and R. L. Culp. 1979. Estimating water treatment costs: Cost curves applicable to 2500 gpd to 1 mgd Treatment Plants. Cincinnati, OH.
6 | Harris et al. 1982 |  |  |  | Harris, R. W., M. J. Cullinane, and P. T. Sun. 1982. Process Design and Cost Estimating Algorithms for the Computer Assisted Procedure for Design and Evaluation of Wastewater Treatment Systems (CAPDET). Washington, D.C.: U.S. Environmental Protection Agency.
7 | Hydromantis 2014 |  |  |  | Hydromantis. 2014. CAPDETWorks Version 3.0 Software: Rapid Design and Costing Solution for Wastewater Treatment Plants.
8 | IRS 2018 |  |  |  | IRS. 2018. Internal Revenue Service: Yearly Average Currency Exchange Rates https://www.irs.gov/individuals/international-taxpayers/yearly-average-currency-exchange-rates.
9 | Lavappa et al. 2017 |  |  |  | Lavappa, P. D.; Kneifel, J. D.; O’Rear, E. Energy Price Indices and Discount Factors for Life-Cycle Cost Analysis – 2017 Annual Supplement to NIST Handbook 135; National Instititute of Standards and Technology, 2017.
10 | Macomber 2016 |  |  |  | Macomber, S. Seeing the Big Picture: Huber’s New Q-Press. 2016.
11 | PZP 2014 |  |  |  | PZP. The Price List of Heat Pumps. PZP Heating a.s. 2014.
12 | RSMeans 2016 |  |  |  | RSMeans; Building Construction Cost Data. June 7, 2016.
13 | Scheuer et al. 2003 |  |  |  | Scheuer, C.; Keoleian, G. A.; Reppe, P. Life Cycle Energy and Environmental Performance of a New University Building: Modeling Challenges and Design Implications. Energy Build. 2003, 35, 1049–1064.
14 | SFWPS 2017 |  |  |  | SFWPS (San Francisco Water Power Sewer). 2017. Rates Schedules & Fees for Water Power and Sewer Service (Fiscal Year 2017-2018). San Francisco, CA: San Francisco Public Utilities Commission.
15 | US DOL 2017 |  |  |  | U.S. DOL. May 2016 National Industry-Specific Occupational Employment and Wage Estimates for NAICS 221300 – Water, Sewage and Other Systems; 2017.

## Conversion Factors (hidden)
Conversion Factors, Project Constants, and Looksups used throughout workbook
Conversion Factors
| Category | Parameter | Value | Unit | Source
| Area | sqft/m2 | 10.7639
| Area | ft2/acre | 43560
| Area | ft2/m2 | 10.7639
| Cost | $/kW CHP ICE Capital Cost | 1600 | $/kW | Wiser et al. 2010
| Cost | Maintenance Costs CHP ICE | 0.025 | $/kWh | Wiser et al. 2010
| Density | Water Density | 999.97 | kg/m³
| Density | biogas Density | 1.214 | kg/m3
| Density | Methane Density | 0.656 | kg/m3
| Density | Compost Density | 453.5929 | kg/m3
| Density | water density | 8.338 | lb/gal @ 60*F
| Density | Ferric Chloride | 1.37 | s.g. | http://edwardschemicals.com/MSDS/water-treatment/FERRIC%20CHLORIDE%2038%20-%2042.pdf
| Density | water density | 8.329 | lb/g at 70*F | http://www.engineeringtoolbox.com/water-specific-volume-weight-d_661.html
| Distance | m/mile | 1609.34
| Distance | ft/m | 3.2808
| Distance | km/mile | 1.6093
| Energy | Methane Energy Content | 50 | MJ/kg | http://www.world-nuclear.org/information-library/facts-and-figures/heat-values-of-various-fuels.aspx
| Energy | Methane Energy Content | 55 | MJ/kg | http://www.world-nuclear.org/information-library/facts-and-figures/heat-values-of-various-fuels.aspx
| Energy | Natural Gas, energy content | 36.6256 | MJ/m3 | LHV
| Energy | U.S. conventional diesel | 135.5219 | MJ/gal
| Energy | HHV to LHV, generic | 0.9 |  | https://www.csemag.com/single-article/understanding-cogeneration-systems/f4ee71595545969c02674b7b029620a1.html?tx_ttnews%5BsViewPointer%5D=1
| Energy | BTU/Dekatherm (DTH) | 1000000
| Energy | MJ/kWh | 3.6
| Energy | Btu/ft3 | 1027
| Energy | BTU/MJ | 947.817 |  | google conversions
| Energy | 1 MCF = | 1000 | ft3 of natural gas
| Energy | kW/HP | 0.7457
| Energy | Btu/kwh | 3412.1416
| Generic | g/kg, ml/L, etc… | 1000
| Infrastructure | Handrail | 2.7216 | kg/ft
| Volume | gal/3 | 264.1721
| Volume | ft3/m3 | 35.3147
| Volume | gallons/ft3 | 7.4805
| Volume | L/gallon | 3.7854
| Volume | m3/yd3 | 0.76455
| Volume | L/m3 | 1000
| Wastewater Characteristics | BOD/cBOD ratio | 1.16 |  | Source: Brake 2007
| Weight | lb/kg | 2.2046
| Weight | kg per short ton | 907.1847
| Weight | kg/mg | 1e-06
| Time | days per year | 365
| Time | hours per year | 8760 |  | google conversions
| TIme | minutes per hour | 60
| Time | hours per day | 24
| Density of diesel |  | 0.832 | kg/L | MIT Energy Conversions
| Density of solids, wastewater |  | 1400 | kg/m3
| Density of water |  | 1000 | kg/m3
| Food Waste, air filled pore space |  | 0.481 | v/v | Sundberg et al. 2011 | very sensitive to this parameter
| Food Waste, raw, before processing |  | 474.6217 | kg/m3 | MSW DSTool
| Food Waste, raw, before processing |  | 650 | kg/m3 | EC 2013 | not used, for comparison
| Food Waste, heating value |  | 1800 | BTU/lb | MSW DSTool
| Gravity |  | 9.81 | m/s2
| Methane Density | at STP | 0.656 | kg/m3
| Activated Carbon Density | assumes coal | 480 | kg/m3 (originally 48 g/cc) | http://www.ecologixsystems.com/product-activated-carbon.php
| Sodium Hypochlorite s.g. |  | 1.211 | s.g. @68*F | JCI Jones Chem Sheet
| water density |  | 8.329 | lb/g at 70*F | http://www.engineeringtoolbox.com/water-specific-volume-weight-d_661.html
| Sodium Bisulfite s.g. |  | 1.3 | s.g. @68*F | http://www.sfm.state.or.us/cr2k_subdb/MSDS/SODIUM_BISULFITE_38_40_SOLUTION.PDF
| mg/kg |  | 1000000
| Ferric Chloride s.g. |  | 1.37 | s.g. @ 68*F | Range (1.26-1.48), Kemira Iron (III) Chloride MSDS
| kg/ton |  | 907.1847
| Specific Weight of Sand |  | 165.4 | lb/cuft | CAPDET Factor
| Convert NH3-N to NH3 |  | 1.2159
| Convert NO2-N to NO2 |  | 3.2844
| Convert NO3-N to NO3 |  | 4.4266
| Rebar | [5 empty] | Steel Grating
|  | Rod Size | Rod Weight |  |  |  | Bar Size Inches: | Weight Per Sq. Ft: | Sect. Prop. Ft. of Width:
| Rod Number | (in) | (lb per linear foot) | kg/ft |  |  | 3/4 x 3/16 | 5.67 | Sx=0.194 / 1x=0.73
| 2 | 0.250 = 1/4" | 0.17 | 0.077111 |  |  | 1 x 1/8 | 5.15 | Sx=0.228 / 1x=0.114
| 3 | 0.375 = 3/8" | 0.38 | 0.17237 |  |  | 1 x 3/16 | 7.35 | Sx=0.344 / 1x=0.171
| 4 | 0.500 = 1/2" | 0.67 | 0.30391 |  |  | 1-1/4 x 1/8 | 6.2 | Sx=0.358 / 1x=0.223
| 5 | 0.625 = 5/8" | 1.04 | 0.47174 |  |  | 1-1/4 x 3/16 | 9.03 | Sx=0.536 / 1x=0.335
| 6 | 0.750 = 3/4" | 1.5 | 0.68039 |  |  | 1-1/2 x 1/8 | 7.35 | Sx=0.515 / 1x=0.387
| 7 | 0.875 = 7/8" | 2.04 | 0.92533 |  |  | 1-1/2 x 3/16 | 10.94 | Sx=0.773 / 1x=0.579
| 8 | 1.000 = 1" | 2.67 | 1.2111 |  |  | 1-3/4 x 3/16 | 12.62 | Sx=1.052 / 1x=0.902
| 9 | 1.128 = 1 1/8" | 3.4 | 1.5422 |  |  | 2 x 3/16 | 14.3 | Sx=1.375 / 1x=1.375
| 10 | 1.270 = 1 1/4" | 4.3 | 1.9504 |  |  | 2-1/4 x 3/16 | 15.87 | Sx=1.740 / 1x=1.958
| 11 | 1.410 = 1 3/8" | 5.31 | 2.4086 |  |  | 2-1/2 x 3/16 | 17.55 | Sx=2.148 / 1x=2.685
| 14 | 1.693 = 1 3/4" | 7.65 | 3.47 |  |  | http://www.directmetals.com/dm/products/bar-grating/carbon-steel-bar-grating.html
| 18 | 2.257 = 2 1/4" | 13.6 | 6.1689
Pipe Weights
| material/inner diameter | Wt/ft | Unit | Wall thickness | Source
| concrete27 | 322 | lb/ft |  | http://www.theturnerco.com/products/reinforced-concrete-pipe
| metal18 | 93.54 | lb/ft | 0.5 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal8 | 27.73 | lb/ft | 0.312 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal12 | 49.61 | lb/ft | 0.375 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal4 | 11.36 | lb/ft | 0.25 | http://www.saginawpipe.com/steel_pipe.htm#pipechart1
| metal10 | 41.59 | lb/ft | 0.375 | http://www.saginawpipe.com/steel_pipe_chart-2.htm
| metal3 | 8.69 | lb/ft | 0.25 | http://www.saginawpipe.com/steel_pipe.htm#pipechart1
| concrete24 | 265 | lb/ft |  | http://www.theturnerco.com/products/reinforced-concrete-pipe
| metal6 | 21.06 | lb/ft | 0.312 | http://www.saginawpipe.com/steel_pipe.htm#pipechart1
| PVC6 | 3.733 | lb/ft | 0.28 | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
| PVC4 | 2.118 | lb/ft | 0.237 | http://www.usplastic.com/catalog/files/drawings/pipespecs.pdf
GREET Fuel Heating Values
| Fuels |  | Lower Heating Value (LHV) [1] |  |  |  | Higher Heating Value (HHV) [1] |  |  | Density
| Gaseous Fuels @ 32 F and 1 atm |  | Btu/ft3 [2] | Btu/lb [3] | MJ/kg [4] |  | Btu/ft3 [2] | Btu/lb [3] | MJ/kg [4] | grams/ft3
| Natural gas |  | 983 | 20267.2259 | 47.1413 |  | 1089 | 22452.705 | 52.2247 | 22
| Hydrogen |  | 290 | 51682.0289 | 120.2116 |  | 343 | 61127.3652 | 142.1814 | 2.5452
| Still gas (in refineries) |  | 1458 | 20162.6287 | 46.898 |  | 1584 | 21905.078 | 50.9509 | 32.8
| Liquid Fuels |  | Btu/gal [2] | Btu/lb [3] | MJ/kg [4] |  | Btu/gal [2] | Btu/lb [3] | MJ/kg [4] | grams/gal
| Crude oil |  | 129670 | 18351.6428 | 42.6857 |  | 138350 | 19580.0863 | 45.543 | 3205
| Conventional gasoline |  | 116090 | 18679.4122 | 43.448 |  | 124340 | 20006.875 | 46.5357 | 2819
| Reformulated or low-sulfur gasoline |  | 113601.5098 | 18210.6734 | 42.3578 |  | 121848.3804 | 19532.6723 | 45.4327 | 2829.5773
| CA reformulated gasoline |  | 113927.154 | 18271.8133 | 42.5 |  | 122174.4341 | 19594.5248 | 45.5766 | 2828.1932
| U.S. conventional diesel |  | 128450 | 18397.1063 | 42.7914 |  | 137380 | 19676.0954 | 45.7663 | 3167
| Low-sulfur diesel |  | 129487.8476 | 18320.1475 | 42.6124 |  | 138490 | 19593.7864 | 45.5749 | 3206
| Petroleum naphtha |  | 116920 | 19320.1249 | 44.9383 |  | 125080 | 20668.5017 | 48.0746 | 2745
| NG-based FT naphtha |  | 111520 | 19081.2361 | 44.3827 |  | 119740 | 20487.6902 | 47.6541 | 2651
| Residual oil |  | 140352.5222 | 16967.6174 | 39.4664 |  | 150110 | 18147.2268 | 42.2102 | 3752
| Methanol |  | 57250 | 8638.7317 | 20.0936 |  | 65200 | 9838.346 | 22.8838 | 3006
| Ethanol |  | 76330 | 11587.1903 | 26.9516 |  | 84530 | 12831.9822 | 29.847 | 2988
| Butanol |  | 99837 | 14774.8988 | 34.3662 |  | 108458 | 16050.7224 | 37.3337 | 3065
| Acetone |  | 83127 | 12721.1795 | 29.5893 |  | 89511 | 13698.1425 | 31.8617 | 2964
| E-Diesel Additives |  | 116090 | 18679.4122 | 43.448 |  | 124340 | 20006.875 | 46.5357 | 2819
| Liquefied petroleum gas (LPG) |  | 84950 | 20037.6862 | 46.6074 |  | 91410 | 21561.4466 | 50.1516 | 1923
| Liquefied natural gas (LNG) |  | 74720 | 20908.2324 | 48.6322 |  | 84820 | 23734.4255 | 55.2059 | 1621
| Dimethyl ether (DME) |  | 68930 | 12416.9812 | 28.8817 |  | 75610 | 13620.3097 | 31.6806 | 2518
| Dimethoxy methane (DMM) |  | 72200 | 10061.1975 | 23.4022 |  | 79196.8954 | 11036.2273 | 25.6701 | 3255
| Methyl ester (biodiesel, BD) |  | 119550 | 16134.0924 | 37.5277 |  | 127960 | 17269.0796 | 40.1676 | 3361
| Fischer-Tropsch diesel (FTD) |  | 123670 | 18593.1307 | 43.2473 |  | 130030 | 19549.3231 | 45.4714 | 3017
| Renewable Diesel I (SuperCetane) |  | 117059 | 18729.0271 | 43.5634 |  | 125294 | 20046.598 | 46.6281 | 2835
| Renewable Diesel II (UOP-HDO) |  | 122887 | 18907.8407 | 43.9794 |  | 130817 | 20127.9793 | 46.8174 | 2948
| Renewable Gasoline |  | 115983 | 18589.6569 | 43.2393 |  | 124230 | 19911.479 | 46.3138 | 2830
| Liquid Hydrogen |  | 30500 | 51621.25 | 120.0703 |  | 36020 | 60963.85 | 141.801 | 268
| Methyl tertiary butyl ether (MTBE) |  | 93540 | 15093.8487 | 35.1081 |  | 101130 | 16318.5901 | 37.9568 | 2811
| Ethyl tertiary butyl ether (ETBE) |  | 96720 | 15612.5355 | 36.3145 |  | 104530 | 16873.2252 | 39.2469 | 2810
| Tertiary amyl methyl ether (TAME) |  | 100480 | 15645.9743 | 36.3923 |  | 108570 | 16905.687 | 39.3224 | 2913
| Butane |  | 94970 | 19465.6314 | 45.2768 |  | 103220 | 21156.6018 | 49.2099 | 2213
| Isobutane |  | 90060 | 19287.2122 | 44.8618 |  | 98560 | 21107.5686 | 49.0959 | 2118
| Isobutylene |  | 95720 | 19271.0319 | 44.8241 |  | 103010 | 20738.7066 | 48.2379 | 2253
| Propane |  | 84250 | 19903.6237 | 46.2955 |  | 91420 | 21597.4989 | 50.2355 | 1920
| Solid Fuels |  | Btu/ton [2] | Btu/lb [5] | MJ/kg [4] |  | Btu/ton [2] | Btu/lb [5] | MJ/kg [4]
| Coal (wet basis) [6] |  | 19546300 | 9773.15 | 22.7322 |  | 20608570 | 10304.285 | 23.9676
| Bituminous coal (wet basis) [7] |  | 22460600 | 11230.3 | 26.1215 |  | 23445900 | 11722.95 | 27.2674
| Coking coal (wet basis) |  | 24600497.1446 | 12300.2486 | 28.6102 |  | 25679670 | 12839.835 | 29.8653
| Farmed trees (dry basis) |  | 16811000 | 8405.5 | 19.5511 |  | 17703170 | 8851.585 | 20.5887
| Herbaceous biomass (dry basis) |  | 14797554.7639 | 7398.7774 | 17.2094 |  | 15582870 | 7791.435 | 18.1228
| Corn stover (dry basis) |  | 14075990 | 7037.995 | 16.3703 |  | 14974460 | 7487.23 | 17.4152
| Forest residue (dry basis) |  | 13243490 | 6621.745 | 15.4021 |  | 14164160 | 7082.08 | 16.4728
| Sugar cane bagasse |  | 12947318 | 6473.659 | 15.0576 |  | 14062678 | 7031.339 | 16.3548
| Petroleum coke |  | 25370000 | 12685 | 29.5051 |  | 26920000 | 13460 | 31.3078
Notes:
[1] The lower heating value (also known as net calorific value) of a fuel is defined as the amount of heat released by combusting a specified quantity (initially at 25°C) and returning the temperature of the combustion products to 150°C, which assumes the latent heat of vaporization of water in the reaction products is not recovered.
The higher heating value (also known as gross calorific value or gross energy) of a fuel is defined as the amount of heat released by a specified quantity (initially at 25°C) once it is combusted and the products have returned to a temperature of 25°C, which takes into account the latent heat of vaporization of water in the combustion products.
[2] Btu = British thermal unit.
[3] The heating values for gaseous fuels in units of Btu/lb are calculated based on the heating values in units of Btu/ft3 and the corresponding fuel density values. The heating values for liquid fuels in units of Btu/lb are calculated based on heating values in units of Btu/gal and the corresponding fuel density values.
[4] The heating values in units of MJ/kg, are converted from the heating values in units of Btu/lb.
[5] For solid fuels, the heating values in units of Btu/lb are converted from the heating values in units of Btu/ton.
[6] Coal characteristics assumed by GREET for electric power production.
[7] Coal characteristics assumed by GREET for hydrogen and Fischer-Tropsch diesel production.
Source:
GREET Transportation Fuel Cycle Analysis Model, GREET 1.8b, developed by Argonne National Laboratory, Argonne, IL, released September 5, 2008. https://greet.es.anl.gov/
| Year | CPI | Year | CPI
| 1970 | 38.8 | 1994 | 148.2
| 1971 | 40.5 | 1995 | 152.4
| 1972 | 41.8 | 1996 | 156.9
| 1973 | 44.4 | 1997 | 160.5
| 1974 | 49.3 | 1998 | 163
| 1975 | 53.8 | 1999 | 166.6
| 1976 | 56.9 | 2000 | 172.2
| 1977 | 60.6 | 2001 | 177.1
| 1978 | 65.2 | 2002 | 179.9
| 1979 | 72.6 | 2003 | 184
| 1980 | 82.4 | 2004 | 188.9
| 1981 | 90.9 | 2005 | 195.3
| 1982 | 96.5 | 2006 | 201.6
| 1983 | 99.6 | 2007 | 207.3
| 1984 | 103.9 | 2008 | 215.3
| 1985 | 107.6 | 2009 | 214.5
| 1986 | 109.6 | 2010 | 218.1
| 1987 | 113.6 | 2011 | 224.9
| 1988 | 118.3 | 2012 | 229.6
| 1989 | 124 | 2013 | 233
| 1990 | 130.7 | 2014 | 236.7
| 1991 | 136.2 | 2015 | 237
| 1992 | 140.3 | 2016 | 240
| 1993 | 144.5 | 2017 | n.a.
Source: BLS Detailed Report 2017
Note on D8: Ben Morelli: rane of 465 to 1600 for lean burn or 465 to 1200 for advanced generation

## Lookups (hidden)
Treatment Systems
RVFW
AeMBR
AnMBR
All
All MBR
General Cost Category
Labor
Materials
Energy
Chemical
Capital
Wastewater Type
Mixed WW
Graywater
Both
System Scale
Building
District
Both
Detailed Cost Category
Labor
General
Materials
Diesel
Natural Gas
Water
Chemicals
Fee Revenue
Renewable Energy Credit
Capital
Electricity
Alternative Energy Credit
Operations Labor
Maintenance Labor
Units
$/yr
$/replacement
$
Timing
Annual
Replace at Lifespan
Year 1
Process
Equalization
Clarification
Fine Screen
Wetland
AeMBR
AnMBR
Dewatering
Disposal to Sewer
Thermal Recovery
Composting
Ozone
UV
Chlorination
Miscellaneous
Administration
Storage
Building Reuse
Zeolite
Avoided Utility Costs
DHS
System Size
Building
District
All
Sewer Scenario
Sewered
Unsewered
Both
Reuse Scenario
Both
Low Reuse
High Reuse

## Supporting Info (hidden)
Direct Cost Factors
Direct Cost Elements | Direct Cost Factor
Mobilization | 0.05
Site Preparation | 0.07
Site Electrical | 0.15
Yard Piping | 0.1
Instrumentation and Control | 0.08
Lab and Administration Building | n.a.
Indirect Cost Factors
Indirect Cost Elements | Indirect Cost Factor
Miscellaneous Costs | 0.05
Legal Costs | 0.02
Engineering Design Fee | 0.15
Inspection Costs | 0.02
Contingency | 0.1
Technical | 0.02
Contractor Overhead and Profit | 0.15
Summary of Included Costs
Process | Capital Cost | Installation Cost | Direct/Indirect | O&M Material | Operation Labor | Maintanence Labor
Fine Screen | Yes | Yes | Yes | Yes | Yes | Yes
Equalization | Yes | Yes | Yes | Yes | Yes (use maintenance as a proxy) | Yes
Clarification | Yes | Yes | Yes | Yes | Yes | Yes
Sludge Pumping | Yes | Yes | Yes | Yes | excluded, minor | Yes
AeMBR | Yes | Yes | Yes | Yes | Yes | Yes
AnMBR | Yes | Yes | Yes | Yes | Yes | Yes
RVFW | Yes | Yes | Yes | Yes | Yes | Yes
Reuse Pipe and Pumps | Yes | Yes | Excluded | Yes | Excluded | Yes
Ozone | Yes | Yes | Yes | Yes | Yes | Yes
Chlorination | Yes | Yes | Yes | Yes | Yes | Yes
Thermal Recovery | yes | yes | yes | Yes | excluded, minor | yes
Dewatering | Yes | Yes | Yes | Yes | Yes | Yes
DHS | Yes | Yes | Yes | Yes | Yes | Yes
Zeolite | Yes | Yes | Yes | Yes | Yes | Yes
UV | Yes | Yes | Yes | Yes | Yes | Yes
Process | AeMBR, Build, WW | AeMBR, Build, GW | AnMBR, Build, WW | AnMBR, Build GW | RVFW, Build, WW | RVFW, Build, GW | AeMBR, Dist, WW | AeMBR, Dist, GW
Fine Screen | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Equalization | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Clarification |  |  |  |  | Yes | Yes
Sludge Pumping | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
AeMBR | Yes | Yes |  |  |  |  | Yes | Yes
AnMBR |  |  | gas cleaning (not included) | gas cleaning (not included)
RVFW |  |  |  |  | Yes | Yes
Reuse Pipe and Pumps | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Ozone |  |  |  |  | Yes
Chlorination | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Thermal Recovery | Yes | Yes
DHS |  |  | Yes | Yes
Zeolite |  |  | Yes | Yes
UV | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
NPV Calculation Formual Summary
NPV is summed for each system using a series of sumifs statements. The following table lists all the possible combinations of parameter values and the line of code that captures those values.
Table columns titled: "general cost category" and "Process" are the same throughout the formula.
Other columns are not part of the sumifs statement.
Reuse Scenario | Sewer Scenario | System Size | Treatment System | Wastewater Type | Code Line Number (sumif row)
Both | Sewered | Building | RVFW | Mixed WW | line1
Both | Sewered | Building | RVFW | Both | line 5
Both | Both | All | All | Both | line6
Both | Sewered | Building | All | Mixed WW | line 7
Both | Both | Both | All | Mixed WW | line 8
Both | Both | Both | All | Both | line 9
Both | Sewered | Building | All | Graywater | line 7
Both | Sewered | Building | RVFW | Graywater | line1
Both | Sewered | Building | All MBR | Mixed WW | line 10
Both | Sewered | Building | AeMBR | Mixed WW | line1
Both | Sewered | Building | AeMBR | Graywater | line1
Both | Sewered | Building | AnMBR | Mixed WW | line1
Both | Sewered | Building | AnMBR | Graywater | line1
Both | Sewered | Building | All MBR | Graywater | line 10
Both | Both | District | AeMBR | Mixed WW | line 2
Both | Sewered | District | AeMBR | Mixed WW | line1
Both | Both | District | All MBR | Mixed WW | line 11
Both | Both | District | All MBR | Both | line 12
Both | Sewered | District | AeMBR | Graywater | line1
Both | Sewered | District | All MBR | Graywater | line 10
Both | Sewered | Building | AnMBR | Both | line 5
Both | Sewered | District | All | Graywater | line 7
Both | Both | District | All | Mixed WW | line 13
Both | Both | District | AeMBR | Both | line 14
Both | Unsewered | District | AeMBR | Mixed WW | line1
Low Reuse | Sewered | Building | All | Mixed WW | line 3
Low Reuse | Sewered | Building | All | Graywater | line 4
Low Reuse | Both | District | All | Mixed WW | line 4
Low Reuse | Both | District | All | Graywater | line 4
High Reuse | Sewered | Building | All | Mixed WW | line 3
High Reuse | Sewered | Building | All | Graywater | line 3
High Reuse | Both | District | All | Mixed WW | line 4
High Reuse | Both | District | All | Graywater | line 4

## Checks (hidden)
Full Plant
Wetland system capital cost is approximately 1 million dollars.
Ozone
Construction cost for a 5 lb and 10 lb ozone generating system was 33,560 and 45,280 in 1979 dollars or approximately $100,000 and 131,883 in 2016 dollars (Hansen et al. 1979).
Total installed cost for the RVFW, mixed wastewater system is ~ $120,000 and has a generation capacity of ~8 lb/day.
Process energy for a a 5 lb ozone generation system was estimted to be 21,000 kWh in 1979. Our system produces an average of 4.3 lb ozone per day and consumes 7900 kWh. The equipment is expected to have improved significantly since 1979. (Hansen et al. 1979)
Contact Basins
Cost of an 850 gallon Cl contact basin was $1,020 in 1979, or $2,912 in 2016 dollars (Hansen et al. 1979), our estimate for a 600-1,200 gallon tank is $3360. Excluding direct and indirect cost of system interconnection.
UV System Cost
EPA estimates the cost of a 0.025 MGD system to be 3750 in 1999 (U.S. EPA 2002)
| 2016 cost would be | 5402.1609
Our system cost is ~$8,000
U.S. EPA. Wastewater Technology Fact Sheet - Disinfection for Small Systems. (2002).