## Cover
Building and District Scale Wastewater Treatment for Reuse Applications: MBR Thermal Recovery
Prepared by:
Ben Morelli and Sarah Cashman
Eastern Research Group
110 Hartwell Avenue
Lexington, MA 02421-3136
Last Updated: 6/11/2019
*sarah.cashman@erg.com

## TOC
Table of Contents
| LCI | Linked thermal recovery LCI information for the mixed WW and graywater treatment scenarios.
| Heat Pump | Heat pump calculations used to size heat pumps and calculate LCI values.
| Building Hot Water | Documents calculations used to verify the thermal recovery scenario LCI values. Calculates the fraction of hot water heat that can be provided by wastewater and graywater.
| Sources | Documents sources used in workbook.
Hidden | Report Table | Linked report table.

## LCI
LCI - Wastewater
Unit Process | Input/Output | Description | Quantity | Quantity Units | Lifespan | Annual Quantity | Quantity per m3
Thermal Recovery | Electricity | Operation Energy | 145561.6791 | kWh | 1 | 145561.6791 | 4.2112
Thermal Recovery | Natural Gas | Avoided | 30661.4455 | m3 | 1 | 30661.4455 | 0.88705
Thermal Recovery | Electricity | Avoided | 255916.0312 | kWh | 1 | 255916.0312 | 7.4038
Thermal Recovery | R-134a | Annual Emissions | 0.53043 | kg | 1 | 0.34484 | 9.9764e-06
Thermal Recovery | Infrastructure | Steel | 271.7977 | kg | 20 | 13.5899 | 0.00039316
Thermal Recovery | Infrastructure | Copper | 62.9426 | kg | 20 | 3.1471 | 9.1048e-05
Thermal Recovery | Infrastructure | Electricity | 267.824 | kWh | 20 | 13.3912 | 0.00038741
Thermal Recovery | Infrastructure | Natural Gas Combustion | 61.6981 | m3 | 20 | 3.0849 | 8.9248e-05
Thermal Recovery | Infrastructure | Elastomere | 28.6103 | kg | 20 | 1.4305 | 4.1386e-05
Thermal Recovery | R-134a | Manufacturing emissions | 0.26522 | kg | 20 | 0.013261 | 3.8364e-07
* Heat pump lifespan from Greening and Azapagic 2012.
LCI - Graywater
Unit Process | Input/Output | Description | Quantity | Quantity Units | Lifespan | Annual Quantity | Quantity per m3
Thermal Recovery | Electricity | Operation Energy | 90774.5738 | kWh | 1 | 90774.5738 | 4.1034
Thermal Recovery | Natural Gas | Avoided | 19933.2003 | m3 | 1 | 19933.2003 | 0.90106
Thermal Recovery | Electricity | Avoided | 166372.6358 | kWh | 1 | 166372.6358 | 7.5207
Thermal Recovery | R-134a | Annual Emissions | 0.34484 | kg | 1 | 0.34484 | 1.5588e-05
Thermal Recovery | Infrastructure | Steel | 176.6974 | kg | 20 | 8.8349 | 0.00039937
Thermal Recovery | Infrastructure | Copper | 40.9194 | kg | 20 | 2.046 | 9.2486e-05
Thermal Recovery | Infrastructure | Electricity | 174.1141 | kWh | 20 | 8.7057 | 0.00039353
Thermal Recovery | Infrastructure | Natural Gas Combustion | 40.1103 | m3 | 20 | 2.0055 | 9.0657e-05
Thermal Recovery | Infrastructure | Elastomere | 18.5997 | kg | 20 | 0.92999 | 4.2039e-05
Thermal Recovery | R-134a | Manufacturing emissions | 0.17242 | kg | 20 | 0.008621 | 3.897e-07

## Heat Pump
Calculate recovered thermal energy from Wastewater (WW) and Graywater (GW)
Influent Wastewater Characteristics
| Graywater temperature (high strength) - Celsius (Tww, ei) | 30 | °C
| Mixed wastewater temperature (all strengths) - Celsius (Tww,ei) | 23 | °C
| Graywater Flowrate | 0.016 | MGD
| Mixed WW Flowrate | 0.025 | MGD
| Graywater Flowrate | 22121.9465 | m3/yr
| Mixed WW Flowrate | 34565.5414 | m3/yr
| Density of water (kg/L); rho | 1 | Meggers and Leibundgut, 2011
| Graywater Mass Flowrate | 0.701 | kg/sec
| Mixed WW Mass Flowrate | 1.0953 | kg/sec
| Combined coefficient of performance GW1 | 2.57 | Kahraman and Celebi 2009, Average of CP I for 30 degrees C
| Combined coefficient of performance WW1 | 2.48 | Kahraman and Celebi 2009, Average of CP I for 20 degrees C
| Compressor COP, GW | 3.1 | Studer 2007
| Compressor COP, WW | 2.9914 | Studer 2007 scaled based on temperture difference.
1 80% of maximum COP. Assumes system continually feeds potable water from centralized drinking water system maintaining a high condenser ΔT.
| Specific heat of water (cp) | 4180 | J/kg-°C (Meggers and Leibundgut, 2011)
| Evaporator side Inlet-outlet difference, GW (Δte, GW) | 4.3 | °C (Kahraman and Celebi 2009), average of CP I for 30*C
| Evaporator side Inlet-outlet difference, WW (Δte, WW) | 4.16 | °C (Kahraman and Celebi 2009), average of CP I for 20*C
| Temperature of graywater at evaporator exit(Tgw, ee) | 25.7 | °C (calculated)
| Temperature of wastewater at evaporator exit(Tww, ee) | 18.84 | °C (calculated)
| Graywater, Obtainable thermal power | 12.5998 | kW
| Wastewater, Obtainable thermal power | 19.0462 | kW
| heat transfer coefficient adopted for wastewater with organic origin | 850 | W/m2-°K (Cipolla 2014)
| Graywater Exchanger Area | 5.1709 | m2 (includes safety factor of 1.5) (Cipolla 2014)
| WW Exchanger Area | 7.8165 | m2 (includes safety factor of 1.5) (Cipolla 2014)
| GW, compressor power | 5.9999 | kW
| WW, compressor power | 9.5641 | kW
| GW, compressor and Pump Power | 8.0254 | kW
| WW, compressor and Pump Power | 12.8691 | kW
| Total Output Power, GW | 18.5997 | kW (Cipolla 2014)
| Total Output Power, WW | 28.6103 | kW (Cipolla 2014)
| ΔTc, gw | 6.3476 | °C (calculated)
| ΔTc, ww | 6.2489 | °C (calculated)
| ΔTc, gw | 6.35 | °C (Kahraman and Celebi 2009) | [calculated values should match these values]
| ΔTc, ww | 6.25 | °C (Kahraman and Celebi 2009) | [calculated values should match these values]
| Compressor Efficiency | 0.775 | average of max and min reciprocating and rotary screw compressor efficiencies
| Annual Electricity Consumption, Compressor and Pumps, GW | 90774.5738 | kWh, electricity
| Annual Electricity Consumption, Compressor and Pumps, WW | 145561.6791 | kWh, electricity
| Total thermal energy to hot water storage, GW | 163045.1831 | kWh, thermal energy
| Total thermal energy to hot water storage, WW | 250797.7106 | kWh, thermal energy
| Heat pump storage standby loss | 5.612%
| Delivered thermal energy (exclude distribution loss), GW | 153894.6881 | kWh, thermal energy
| Delivered thermal energy (exclude distribution loss), WW | 236722.3289 | kWh, thermal energy
| Recovered Energy, GW | 2.8533 | kWh/m3 wastewater
| Recovered Energy, WW | 2.6373 | kWh/m3 wastewater
Scenario 2: Avoided Natural Gas Combustion
| Natural Gas Energy per unit volume | 40.575 | MJ/m3 (HHV), U.S.DOE 2017
| Natural Gas Energy per unit mass | 52.225 | MJ/kg (HHV), U.S. DOE 2017
| Gas Storage Water Heater Energy Factor | 0.685 | Hoeschele et al. 2012
| Avoided Natural Gas, GW | 19933.2003 | m3 natural gas/year
| Avoided Natural Gas, WW | 30661.4455 | m3 natural gas/year |  | Link to compressor efficiency ranges
* HHV should be used to calculate natural gas hot water heater thermal efficiency calculations (CFR 10, Chapter 2, Subpart D, Part 431)
Scenario 2: Avoided Electricity Use
| Electric Hot Water Heater Thermal Efficiency | 0.98
| Energy Factor | 0.925 | Hoeschele et al. 2012
| Avoided Electricity, GW | 166372.6358 | kWh/year
| Avoided Electricity, WW | 255916.0312 | kWh/year
https://www.ecfr.gov/cgi-bin/retrieveECFR?gp=&SID=704e762f2e5e5c763c0e2fd418837cef&mc=true&n=sp10.3.431.g&r=SUBPART&ty=HTML
Refrigerant Emissions (GHG)
| During Manufacture | 3% | Greening and Azapagic 2012
| During Annual Operation | 6% | Greening and Azapagic 2012
| During Manufacture | 0.0927 | kg over lifespan (20 years)
| During Annual Operation | 0.1854 | kg per year
Infrastructure
per 10 kW of Heat pump capacity for a water source heat pump (Greening and Azapagic 2012)
| Low alloy steel | 20 | kg
| Reinforcing steel | 75 | kg
| Copper | 22 | kg
| R-134a | 3.09 | kg
| Elastomere | 10 | kg
| PVC | 1 | kg
| Polyolester oil | 1.7 | kg (exlcuded)
| Assembly Electricity | 93.6111 | kWh
| Assembly Natural Gas | 875 | MJ
Heat Pump
Water Heater (i.e., condensor)
Heating Element (e.g., radiator, hot water for sinks/showers)
Evaporator (Refrigerant to Vapor)
Recycled Water in
(T = X)
Refrigerant (liquid)
Copper coil in water tank to transmit heat. Starts as hot vapor refrigerant. As refrigerant flows through the water heater, it releases its heat and compresses back to a liquid.
Recycled Water Out
(T = Y)
Potable Water in
Graywater or mixed WW Treatment
Compressor (pressure heats refrigerant vapor)
Expansion Valve (reduces pressure and temperature)
Electricity (1 kW consumed, 4 kW produced)

## Building Hot Water
Check Quantity of Recovered Thermal Energy
Recovered Thermal Heat
| Graywater Scenario | 72270.6092 | kWh
| Wastewater Scenario | 105236.0315 | kWh
| GW Thermal Energy Share of Total Hot Water Energy Demand1 | 8.614% | calculated
| WW Thermal Energy Share of Total Hot Water Energy Demand | 12.54% | calculated
1 GW thermal energy recovery can provide between 16 and 55% of the DHW load (Eslami-nejad and Bernier 2009)
| Water Temperature, to building (potable) | 14.6 | °C (calculated)
| Hot Water Temperature, to units | 55 | °C (Meggers and Leibundgut, 2011)
| Specific heat of water (cp) | 4180 | J/kg-°C (Meggers and Leibundgut, 2011)
| ΔT | 40.4 | °C (calculated)
| Residential Hot water use | 0.0061623 | MGD
| DHW Mass Flowrate | 0.26998 | kg/sec
| Power required to provide daily water heat | 45.5928 | kW
| Electricity Demand (excluding heater efficiency) | 399666.863 | kWh
| Building Residents | 516 | persons
| Hot water flow per resident | 45.2067 | liters/peson/day
| DHW Electricity demand per resident | 3.0754 | kWh/peson/day
| Office hot water use1 | 0.0027638 | MGD
| HW Mass Flowrate | 0.12109 | kg/sec
| Power required to provide daily water heat | 20.4487 | kW
| Electricity Demand (excluding heater efficiency) | 179253.1802 | kWh
| Building Office Workers | 585 | persons
| Hot water flow per office worker | 17.884 | liters/peson/day
| DHW Electricity demand per household | 0.8395 | kWh
1 5 gallons per worker per day, of 10.6 gallons total use (~42% is used as hot water)
| Total power required to provide daily water heat | 66.0415 | kW
| Gas Water Heater Efficiency | 0.69
| Annual Electricity Consumption | 839014.5554 | kWh/year
| Annual Electricity Consumption | 23.766 | kWh/m2
| Typical water heating energy requirement (all buildings) | 20 to 40 | kWh/m2/yr (Meggers and Leibundgut, 2011)

## Sources
Citation | Reference
Meggers and Leibundgut, 2011 | Meggers, F. and H. Leibundgut. 2011. The potential of wastewater heat and exergy: Decentralized high temperature recovery with a heat pump. Energy and Buildings 43: 879-886
Eslami-nejad and Bernier 2009 | Eslami-nejad, P., and M. Bernier. 2009. Impact of grey water heat recovery on the electrical demand of domestic hot water heaters. In Building Simulation, 681–687.
Studer 2007 | Studer, U. 2007. Heat recovery from raw sewage - An alternative for thermal energy supply in cities. In Proceedings of Clima 2007 WellBeing Indoors, 7. Helsinki, Finland.
Greening and Azapagic 2012 | Greening, B., and A. Azapagic. 2012. Domestic heat pumps: Life cycle environmental impacts and potential implications for the UK. Energy 39. Elsevier Ltd: 205–217. doi:10.1016/j.energy.2012.01.028.
Cipolla and Maglionico 2014 | Cipolla, S. S., and M. Maglionico. 2014. Heat recovery from urban wastewater: Analysis of the variability of flow rate and temperature in the sewer of Bologna, Italy. Energy Procedia 45. Elsevier B.V.: 288–297. doi:10.1016/j.egypro.2014.01.031.
Hoeschele et al. 2012 | Hoeschele, M., D. Springer, A. German, J. Staller, and Y. Zhang. 2012. Strategy Guideline: Proper Water Heater Selection.
U.S.DOE 2017 | U.S. DOE. GREET® Model. U.S. Department of Energy 2017.

## Report Table (hidden)
Parameter | Wastewater | Graywater | Units
Mass Flowrate | 1.0953 | 0.701 | kg/sec
Temperature, in evaporator | 23 | 30 | °C
Temperature, out evaporator1 | 18.84 | 25.7 | °C
ΔT, evaporator | 4.16 | 4.3 | °C
Water specific heat | 4180 |  | J/kg-°C
Obtainable thermal power | 19.0462 | 12.5998 | kW
Compressor coefficient of performance | 2.9914 | 3.1
Combined coefficient of performance | 2.48 | 2.57
Compressor power | 12.8691 | 8.0254 | kW
Compressor efficiency | 0.775
Heat pump electricity consumption | 146000 | 91000 | kWh/year
ΔT, condenser | 6.2489 | 6.3476 | °C
Delivered thermal energy | 237000 | 154000 | kWh/year
Recovered thermal energy | 2.6373 | 2.8533 | kWh/m3
Avoided natural gas | 31000 | 20000 | m3/year
Avoided electricity | 256000 | 166000 | kWh/year