## Sheet1
Table 3. Example values for key WBS model inputs for nitrate removal
Technology | Input | Value Selected to Generate Example Costs
|  | Influent concentration 90 mg/L as nitrate | Influent concentration 195 mg/L as nitrate
Anion Exchange | Resin type | Nitrate-selective | Nitrate-selective
| Number of bed volumes before regeneration | 420 | 260
| Vessel configuration | Parallel | Parallel
| Empty bed contact time | 2 minutes | 3 minutes
| Discharge option for spent brine | Publicly owned treatment works | Publicly owned treatment works
Biological Treatment | Design type | Fluidized bed | Fluidized bed
| Electron donor requirements | 28.5 mg/L acetic acid | 40.6 mg/L acetic acid
| Biomass generation | 11.3 mg/L | 14.9 mg/L
| Nutrient requirements | 2 mg/L phosphoric acid (as phosphorus) | 2 mg/L phosphoric acid (as phosphorus)
| Empty bed contact time | 10 minutes | 10 minutes
| Post-treatment options | Aeration and polishing filter | Aeration and polishing filter
| Discharge option for spent backwash | Recycle | Recycle
POU/POE Treatment | Technology | POU reverse osmosis (purchased) | POU reverse osmosis (purchased)
| Water source | Groundwater | Groundwater
| Include UV disinfection | No | No
WBS – work breakdown structure; POU/POE – point-of-use/point-of entry; POU – point-of-use; UV – ultraviolet

## Data
| Discount Rate | 7%
| Component Level | low
|  | Annualized Costs ($2017) |  |  |  |  | $/kgal |  |  |  |  | AX - LO |  |  | AX - HI |  |  | BIO - LO |  |  | BIO - HI |  |  | POU
Average Flow (MGD) | Design Flow (MGD) | Anion exchange - lower influent nitrate | Anion exchange - higher influent nitrate | Biological treatment - lower influent nitrate | Biological treatment - higher influent nitrate | POU reverse osmosis | Anion exchange - lower influent nitrate | Anion exchange - higher influent nitrate | Biological treatment - lower influent nitrate | Biological treatment - higher influent nitrate | POU reverse osmosis | TC | OM | UL | TC | OM | UL | TC | OM | UL | TC | OM | UL | TC | OM | UL
0.007 | 0.03 | 18307.2895 | 20162.8652 | 95852.6164 | 96016.4391 | 7927.7516 | 7.1653 | 7.8915 | 37.5157 | 37.5798 | 3.1028 | 103125 | 7314 | 15.8 | 103909 | 9086 | 15.8 | 671104 | 37627 | 24.3 | 671344 | 37770 | 24.3 | 11538 | 6285 | 10
0.009 | 0.038 | 19227.6931 | 21277.1398 | 95599.4393 | 95808.8269 | 9531.3549 | 5.8532 | 6.4771 | 29.1018 | 29.1655 | 2.9015 | 104095 | 8131 | 15.8 | 106041 | 9973 | 15.8 | 667002 | 37823 | 24.4 | 667272 | 38009 | 24.4 | 14450 | 7474 | 10
0.012 | 0.049 | 20493.5025 | 22859.9176 | 97472.3458 | 97826.4961 | 11829.5029 | 4.6789 | 5.2192 | 22.254 | 22.3348 | 2.7008 | 104975 | 9303 | 15.8 | 112386 | 10963 | 16 | 683094 | 38302 | 24.4 | 684331 | 38549 | 24.4 | 18609 | 9180 | 10
0.016 | 0.063 | 21915.9384 | 24755.9697 | 101800.9171 | 102511.0823 | 14813.4805 | 3.7527 | 4.239 | 17.4317 | 17.5533 | 2.5366 | 113926 | 9856 | 16 | 115041 | 12578 | 16 | 717993 | 39707 | 24.5 | 721406 | 40122 | 24.5 | 24017 | 11394 | 10
0.022 | 0.081 | 23488.9384 | 27233.0603 | 104637.3604 | 105298.5748 | 18723.3742 | 2.9251 | 3.3914 | 13.0308 | 13.1131 | 2.3317 | 113926 | 11429 | 16 | 121032 | 14465 | 16.1 | 740065 | 41132 | 25 | 741699 | 41653 | 25 | 31089 | 14297 | 10
0.028 | 0.103 | 25331.4313 | 29879.4083 | 107406.7166 | 108007.503 | 23315.8126 | 2.4786 | 2.9236 | 10.5095 | 10.5682 | 2.2814 | 117841 | 12900 | 16.1 | 124198 | 16822 | 16.2 | 760393 | 42157 | 25 | 760845 | 42719 | 25 | 39408 | 17705 | 10
0.035 | 0.124 | 27266.8397 | 31995.8697 | 110490.1407 | 111419.3096 | 27914.3935 | 2.1344 | 2.5046 | 8.6489 | 8.7217 | 2.1851 | 122490 | 14389 | 16.2 | 131313 | 18237 | 16.3 | 783148 | 43390 | 25.1 | 784889 | 44170 | 25.1 | 47728 | 21119 | 10
0.046 | 0.159 | 30002.3583 | 35886.6124 | 116328.5663 | 117447.5457 | 35499.8094 | 1.7869 | 2.1374 | 6.9284 | 6.9951 | 2.1143 | 125805 | 16776 | 16.2 | 136615 | 21620 | 16.4 | 826168 | 46066 | 25.6 | 828637 | 46975 | 25.6 | 61455 | 26750 | 10
0.06 | 0.203 | 33131.7589 | 41699.4322 | 121490.9854 | 122931.5371 | 45137.4292 | 1.5129 | 1.9041 | 5.5475 | 5.6133 | 2.0611 | 135745 | 18956 | 16.4 | 148730 | 26219 | 16.5 | 864604 | 48066 | 25.7 | 866471 | 49348 | 25.7 | 78927 | 33900 | 10
0.079 | 0.26 | 37716.9298 | 48937.7773 | 129615.6272 | 131343.3671 | 57792.884 | 1.308 | 1.6972 | 4.4951 | 4.555 | 2.0043 | 143710 | 22759 | 16.5 | 161258 | 32316 | 16.8 | 916510 | 52005 | 25.9 | 918420 | 53571 | 25.9 | 101806 | 43298 | 10
0.094 | 0.305 | 41138.4322 | 55357.2809 | 135821.7846 | 138071.0679 | 68140.0485 | 1.199 | 1.6134 | 3.9587 | 4.0242 | 1.986 | 148730 | 25658 | 16.5 | 175665 | 37308 | 16.9 | 956360 | 54951 | 26 | 959781 | 56911 | 26 | 120525 | 50980 | 10
0.123 | 0.39 | 48747.1549 | 66668.0961 | 145684.1429 | 148525.8058 | 87436.0032 | 1.0858 | 1.485 | 3.245 | 3.3083 | 1.9476 | 166908 | 31543 | 16.8 | 197994 | 46514 | 17.2 | 1021239 | 59205 | 25.9 | 1024380 | 61657 | 25.8 | 155467 | 65301 | 10
0.162 | 0.5 | 58074.0603 | 80755.8559 | 160272.1176 | 164233.3198 | 112715.913 | 0.98214 | 1.3657 | 2.7105 | 2.7775 | 1.9062 | 183969 | 39231 | 17 | 217912 | 58642 | 17.3 | 1118144 | 65587 | 25.9 | 1124665 | 68996 | 25.9 | 201225 | 84066 | 10
0.213 | 0.64 | 70018.541 | 97057.9334 | 175214.7346 | 180498.4188 | 145100.7807 | 0.90062 | 1.2484 | 2.2537 | 2.3217 | 1.8664 | 204885 | 49163 | 17.2 | 230451 | 74340 | 18.3 | 1197728 | 74216 | 26.2 | 1207911 | 78641 | 26.2 | 259878 | 108100 | 10
0.25 | 0.74 | 78631.0386 | 110253.9303 | 187927.3875 | 193957.6132 | 168821.0871 | 0.86171 | 1.2083 | 2.0595 | 2.1256 | 1.8501 | 219116 | 56395 | 17.3 | 247625 | 85910 | 18.4 | 1276043 | 80473 | 26.3 | 1284557 | 85637 | 26.2 | 302724 | 125720 | 10
0.329 | 0.947 | 95324.2467 | 138721.4739 | 213122.5764 | 220764.0384 | 217774.3034 | 0.79381 | 1.1552 | 1.7748 | 1.8384 | 1.8135 | 235161 | 72142 | 18.3 | 282437 | 111179 | 18.7 | 1432211 | 92351 | 26.2 | 1441834 | 99181 | 26.2 | 391328 | 162058 | 10
0.349 | 0.999 | 100086.7253 | 145114.4378 | 217029.1878 | 225145.312 | 230149.5292 | 0.7857 | 1.1392 | 1.7037 | 1.7674 | 1.8067 | 241357 | 76359 | 18.4 | 287164 | 117111 | 18.7 | 1441486 | 95643 | 26.3 | 1451099 | 102781 | 26.2 | 413791 | 171235 | 10
0.35 | 1 | 192846.5425 | 255019.9824 | 343360.8812 | 353042.5478 |  | 1.5096 | 1.9962 | 2.6878 | 2.7635 |  | 876498 | 121993 | 29.7 | 1038096 | 171617 | 30.3 | 2438636 | 149667 | 31.5 | 2459607 | 157683 | 31.5
0.42 | 1.181 | 211564.0976 | 273717.038 | 351146.5771 | 362084.5058 |  | 1.3801 | 1.7855 | 2.2906 | 2.3619 |  | 921410 | 137080 | 29.7 | 1025742 | 191866 | 31 | 2421528 | 158458 | 31.3 | 2438656 | 168033 | 31.3
0.505 | 1.394 | 233919.7663 | 313202.4286 | 375823.2235 | 387124.6427 |  | 1.2691 | 1.6992 | 2.0389 | 2.1002 |  | 973721 | 155207 | 29.7 | 1125169 | 223586 | 31.2 | 2544327 | 173175 | 31.2 | 2555720 | 183569 | 31.2
0.607 | 1.645 | 262680.3047 | 356884.9349 | 409120.2192 | 422449.2173 |  | 1.1856 | 1.6108 | 1.8466 | 1.9067 |  | 1033996 | 180013 | 30.8 | 1210530 | 260736 | 31.5 | 2733078 | 191841 | 31.4 | 2740224 | 204401 | 31.3
0.729 | 1.941 | 297283.4888 | 408398.9457 | 444541.8752 | 461316.9482 |  | 1.1173 | 1.5348 | 1.6707 | 1.7337 |  | 1110595 | 208745 | 31.1 | 1317270 | 303961 | 31.7 | 2906872 | 213018 | 31.2 | 2925593 | 228302 | 31.2
0.817 | 2.152 | 320143.8835 | 442862.5772 | 471532.3679 | 489738.0277 |  | 1.0736 | 1.4851 | 1.5812 | 1.6423 |  | 1158040 | 227823 | 31.1 | 1381211 | 333453 | 31.8 | 3075716 | 226788 | 31.3 | 3091639 | 243498 | 31.2
0.981 | 2.539 | 371663.0667 | 511245.4177 | 530548.9358 | 551786.7066 |  | 1.038 | 1.4278 | 1.4817 | 1.541 |  | 1284524 | 269637 | 31.5 | 1491970 | 393271 | 32 | 3331048 | 265487 | 31.3 | 3346578 | 285489 | 31.3
1.179 | 2.996 | 422976.5611 | 594906.1568 | 582532.6367 | 608636.3089 |  | 0.9829 | 1.3824 | 1.3537 | 1.4143 |  | 1375231 | 313845 | 31.6 | 1650504 | 464735 | 32.3 | 3586582 | 297400 | 31.4 | 3608483 | 321498 | 31.3
1.417 | 3.536 | 483550.4001 | 687591.931 | 665990.8344 | 697624.2164 |  | 0.93493 | 1.3294 | 1.2877 | 1.3488 |  | 1481610 | 366292 | 31.9 | 1796366 | 545917 | 32.3 | 4067617 | 342616 | 31.4 | 4094475 | 371814 | 31.3
2.044 | 4.923 | 648364.0251 | 934619.0135 | 834778.0718 | 878802.2172 |  | 0.86905 | 1.2527 | 1.1189 | 1.1779 |  | 1788090 | 507098 | 32.1 | 2196466 | 761829 | 32.6 | 4877656 | 446287 | 31.2 | 4906146 | 488042 | 31.2
2.455 | 5.809 | 749910.2258 | 1092779.2867 | 935125.6028 | 989186.1537 |  | 0.83688 | 1.2195 | 1.0436 | 1.1039 |  | 1951890 | 595837 | 32.2 | 2478195 | 899090 | 33.4 | 5372900 | 507981 | 31.4 | 5412419 | 558503 | 31.3
2.949 | 6.855 | 878506.3858 | 1273851.4997 | 1089311.8156 | 1154472.9014 |  | 0.81616 | 1.1835 | 1.012 | 1.0725 |  | 2196042 | 705310 | 32.3 | 2713812 | 1061747 | 33.4 | 6230892 | 593957 | 31.4 | 6278110 | 654904 | 31.3
3.193 | 7.365 | 942649.329 | 1368504.4729 | 1149252.3273 | 1219081.5838 |  | 0.80883 | 1.1742 | 0.98611 | 1.046 |  | 2312828 | 760398 | 32.4 | 2854206 | 1145776 | 33.6 | 6473709 | 634119 | 31.3 | 6523616 | 699977 | 31.3
3.836 | 8.691 | 1102473.0703 | 1620635.8749 | 1309429.9997 | 1393549.0266 |  | 0.7874 | 1.1575 | 0.93521 | 0.99529 |  | 2639603 | 895338 | 32.9 | 3261073 | 1365959 | 33.5 | 7218039 | 735068 | 31.3 | 7276074 | 814569 | 31.3
4.481 | 9.999 | 1259674.7937 | 1863730.8004 | 1475376.594 | 1567702.562 |  | 0.77018 | 1.1395 | 0.90206 | 0.95851 |  | 2862458 | 1035235 | 33 | 3577960 | 1584740 | 33.7 | 8015346 | 838158 | 31.4 | 8014634 | 929953 | 31.3
4.481 | 10 | 1232668.5217 | 1827867.5025 | 1501723.8888 | 1597402.367 |  | 0.75367 | 1.1176 | 0.91817 | 0.97667 |  | 2526877 | 1033380 | 32.3 | 3154218 | 1580950 | 33.2 | 8018536 | 861261 | 30.9 | 8065404 | 953196 | 30.9
5.484 | 12 | 1468461.3388 | 2215221.9486 | 1686779.0522 | 1814655.1677 |  | 0.73362 | 1.1067 | 0.84269 | 0.90658 |  | 2813141 | 1246973 | 32.5 | 3652284 | 1929315 | 33.2 | 8644680 | 994975 | 30.7 | 8757130 | 1113170 | 30.6
5.485 | 12.001 | 1468655.2836 | 2215529.9663 | 1686913.0575 | 1814799.7362 |  | 0.73358 | 1.1066 | 0.8426 | 0.90648 |  | 2813153 | 1247166 | 32.5 | 3652297 | 1929622 | 33.2 | 8644880 | 995093 | 30.7 | 8757212 | 1113308 | 30.6
6.712 | 14.401 | 1777292.4339 | 2660463.4661 | 1981118.4495 | 2136219.9721 |  | 0.72546 | 1.086 | 0.80866 | 0.87197 |  | 3173606 | 1526998 | 32.3 | 4109203 | 2339551 | 33.5 | 9903342 | 1188588 | 30.7 | 10030390 | 1332741 | 30.6
8.215 | 17.282 | 2139285.5607 | 3209010.8205 | 2349154.1792 | 2526569.4258 |  | 0.71346 | 1.0702 | 0.78345 | 0.84262 |  | 3729683 | 1846369 | 32.8 | 4727135 | 2840128 | 33.6 | 11456216 | 1430560 | 30.5 | 11550441 | 1600420 | 30.5
11.066 | 22.614 | 2800148.3625 | 4300182.8601 | 2976611.904 | 3225418.0164 |  | 0.69326 | 1.0646 | 0.73695 | 0.79855 |  | 4465081 | 2450050 | 33 | 6083698 | 3826891 | 34 | 14009934 | 1855445 | 30.7 | 14183992 | 2089217 | 30.6
13.543 | 27.137 | 3428702.6512 | 5227951.8846 | 3565537.9166 | 3867135.6672 |  | 0.69362 | 1.0576 | 0.7213 | 0.78232 |  | 5313354 | 3012430 | 33.1 | 7050987 | 4678993 | 33.9 | 16384842 | 2253039 | 30.6 | 16574599 | 2538134 | 30.5
16.282 | 32.564 | 4104321.055 | 6247535.7739 | 4192853.6786 | 4553479.6128 |  | 0.69062 | 1.0513 | 0.70552 | 0.7662 |  | 6209941 | 3620102 | 33.7 | 8302894 | 5603513 | 34.4 | 18936657 | 2675943 | 30.6 | 19152812 | 3017749 | 30.5
23.446 | 46.892 | 5858011.7812 | 8867930.5544 | 5874513.0067 | 6390544.9344 |  | 0.68452 | 1.0362 | 0.68645 | 0.74675 |  | 8671372 | 5180812 | 33.5 | 11039632 | 8011001 | 34.3 | 26084969 | 3782941 | 30.5 | 26384204 | 4272888 | 30.4
28.136 | 56.271 | 6921210.9143 | 10568927.7521 | 6889539.9313 | 7514929.002 |  | 0.67395 | 1.0291 | 0.67086 | 0.73176 |  | 9480138 | 6183129 | 33.9 | 12902096 | 9568163 | 34.4 | 29924022 | 4490141 | 30.5 | 30307429 | 5082385 | 30.4
33.762 | 67.525 | 8246641.7889 | 12637179.089 | 8244736.7402 | 8995840.5849 |  | 0.6692 | 1.0255 | 0.66905 | 0.73 |  | 11142439 | 7378479 | 33.8 | 14657714 | 11501066 | 34.5 | 35922625 | 5355734 | 30.2 | 36339181 | 6070380 | 30.1
37.536 | 75.072 | 9181649.4855 | 14362849.522 | 9160273.142 | 9996085.605 |  | 0.67016 | 1.0483 | 0.6686 | 0.72961 |  | 12737827 | 8186094 | 33.4 | 16201861 | 13106135 | 34.4 | 39789172 | 5963521 | 30.3 | 40297603 | 6751955 | 30.1
45.043 | 90.086 | 10928106.6566 | 16930330.0214 | 10820129.0636 | 11828195.2166 |  | 0.6647 | 1.0298 | 0.65813 | 0.71945 |  | 14397040 | 9805500 | 33.7 | 19432894 | 15422997 | 34.4 | 45969026 | 7134193 | 30.5 | 46559495 | 8087500 | 30.3
54.052 | 108.104 | 13102877.0815 | 20212814.3792 | 12900525.8386 | 14098079.0539 |  | 0.66414 | 1.0245 | 0.65389 | 0.71459 |  | 16439536 | 11822967 | 33.9 | 22994018 | 18429259 | 34.4 | 54472134 | 8528467 | 30.4 | 55177759 | 9664973 | 30.3
64.862 | 129.724 | 15980665.1786 | 24302634.0693 | 15300379.5177 | 16737910.1037 |  | 0.67501 | 1.0265 | 0.64628 | 0.707 |  | 19883393 | 14427851 | 33.5 | 27505678 | 22169127 | 34.4 | 64026329 | 10161479 | 30.4 | 64860123 | 11521669 | 30.2
77.834 | 155.669 | 18929413.5291 | 28956401.4988 | 18201607.1981 | 19934483.4834 |  | 0.66631 | 1.0193 | 0.64069 | 0.70169 |  | 23296493 | 17114268 | 33.8 | 31929719 | 26479739 | 34.4 | 75505338 | 12141375 | 30.4 | 76601221 | 13780168 | 30.3
81 | 162 | 19594860.6016 | 30356083.9157 | 18891154.0937 | 20684233.8525 |  | 0.66277 | 1.0268 | 0.63897 | 0.69962 |  | 24495645 | 17684817 | 33.7 | 33405548 | 27761126 | 34.2 | 78238586 | 12605289 | 30.3 | 79335320 | 14303855 | 30.2
Low
[12 empty] | 103125 | 7314 | 15.8 | 103909 | 9086 | 15.8 | 671104 | 37627 | 24.3 | 671344 | 37770 | 24.3
[12 empty] | 104095 | 8131 | 15.8 | 106041 | 9973 | 15.8 | 667002 | 37823 | 24.4 | 667272 | 38009 | 24.4
[12 empty] | 104975 | 9303 | 15.8 | 112386 | 10963 | 16 | 683094 | 38302 | 24.4 | 684331 | 38549 | 24.4
[12 empty] | 113926 | 9856 | 16 | 115041 | 12578 | 16 | 717993 | 39707 | 24.5 | 721406 | 40122 | 24.5
[12 empty] | 113926 | 11429 | 16 | 121032 | 14465 | 16.1 | 740065 | 41132 | 25 | 741699 | 41653 | 25
[12 empty] | 117841 | 12900 | 16.1 | 124198 | 16822 | 16.2 | 760393 | 42157 | 25 | 760845 | 42719 | 25
[12 empty] | 122490 | 14389 | 16.2 | 131313 | 18237 | 16.3 | 783148 | 43390 | 25.1 | 784889 | 44170 | 25.1
[12 empty] | 125805 | 16776 | 16.2 | 136615 | 21620 | 16.4 | 826168 | 46066 | 25.6 | 828637 | 46975 | 25.6
[12 empty] | 135745 | 18956 | 16.4 | 148730 | 26219 | 16.5 | 864604 | 48066 | 25.7 | 866471 | 49348 | 25.7
[12 empty] | 143710 | 22759 | 16.5 | 161258 | 32316 | 16.8 | 916510 | 52005 | 25.9 | 918420 | 53571 | 25.9
[12 empty] | 148730 | 25658 | 16.5 | 175665 | 37308 | 16.9 | 956360 | 54951 | 26 | 959781 | 56911 | 26
[12 empty] | 166908 | 31543 | 16.8 | 197994 | 46514 | 17.2 | 1021239 | 59205 | 25.9 | 1024380 | 61657 | 25.8
[12 empty] | 183969 | 39231 | 17 | 217912 | 58642 | 17.3 | 1118144 | 65587 | 25.9 | 1124665 | 68996 | 25.9
[12 empty] | 204885 | 49163 | 17.2 | 230451 | 74340 | 18.3 | 1197728 | 74216 | 26.2 | 1207911 | 78641 | 26.2
[12 empty] | 219116 | 56395 | 17.3 | 247625 | 85910 | 18.4 | 1276043 | 80473 | 26.3 | 1284557 | 85637 | 26.2
[12 empty] | 235161 | 72142 | 18.3 | 282437 | 111179 | 18.7 | 1432211 | 92351 | 26.2 | 1441834 | 99181 | 26.2
[12 empty] | 241357 | 76359 | 18.4 | 287164 | 117111 | 18.7 | 1441486 | 95643 | 26.3 | 1451099 | 102781 | 26.2
[12 empty] | 876498 | 121993 | 29.7 | 1038096 | 171617 | 30.3 | 2438636 | 149667 | 31.5 | 2459607 | 157683 | 31.5
[12 empty] | 921410 | 137080 | 29.7 | 1025742 | 191866 | 31 | 2421528 | 158458 | 31.3 | 2438656 | 168033 | 31.3
[12 empty] | 973721 | 155207 | 29.7 | 1125169 | 223586 | 31.2 | 2544327 | 173175 | 31.2 | 2555720 | 183569 | 31.2
[12 empty] | 1033996 | 180013 | 30.8 | 1210530 | 260736 | 31.5 | 2733078 | 191841 | 31.4 | 2740224 | 204401 | 31.3
[12 empty] | 1110595 | 208745 | 31.1 | 1317270 | 303961 | 31.7 | 2906872 | 213018 | 31.2 | 2925593 | 228302 | 31.2
[12 empty] | 1158040 | 227823 | 31.1 | 1381211 | 333453 | 31.8 | 3075716 | 226788 | 31.3 | 3091639 | 243498 | 31.2
[12 empty] | 1284524 | 269637 | 31.5 | 1491970 | 393271 | 32 | 3331048 | 265487 | 31.3 | 3346578 | 285489 | 31.3
[12 empty] | 1375231 | 313845 | 31.6 | 1650504 | 464735 | 32.3 | 3586582 | 297400 | 31.4 | 3608483 | 321498 | 31.3
[12 empty] | 1481610 | 366292 | 31.9 | 1796366 | 545917 | 32.3 | 4067617 | 342616 | 31.4 | 4094475 | 371814 | 31.3
[12 empty] | 1788090 | 507098 | 32.1 | 2196466 | 761829 | 32.6 | 4877656 | 446287 | 31.2 | 4906146 | 488042 | 31.2
[12 empty] | 1951890 | 595837 | 32.2 | 2478195 | 899090 | 33.4 | 5372900 | 507981 | 31.4 | 5412419 | 558503 | 31.3
[12 empty] | 2196042 | 705310 | 32.3 | 2713812 | 1061747 | 33.4 | 6230892 | 593957 | 31.4 | 6278110 | 654904 | 31.3
[12 empty] | 2312828 | 760398 | 32.4 | 2854206 | 1145776 | 33.6 | 6473709 | 634119 | 31.3 | 6523616 | 699977 | 31.3
[12 empty] | 2639603 | 895338 | 32.9 | 3261073 | 1365959 | 33.5 | 7218039 | 735068 | 31.3 | 7276074 | 814569 | 31.3
[12 empty] | 2862458 | 1035235 | 33 | 3577960 | 1584740 | 33.7 | 8015346 | 838158 | 31.4 | 8014634 | 929953 | 31.3
[12 empty] | 2526877 | 1033380 | 32.3 | 3154218 | 1580950 | 33.2 | 8018536 | 861261 | 30.9 | 8065404 | 953196 | 30.9
[12 empty] | 2813141 | 1246973 | 32.5 | 3652284 | 1929315 | 33.2 | 8644680 | 994975 | 30.7 | 8757130 | 1113170 | 30.6
[12 empty] | 2813153 | 1247166 | 32.5 | 3652297 | 1929622 | 33.2 | 8644880 | 995093 | 30.7 | 8757212 | 1113308 | 30.6
[12 empty] | 3173606 | 1526998 | 32.3 | 4109203 | 2339551 | 33.5 | 9903342 | 1188588 | 30.7 | 10030390 | 1332741 | 30.6
[12 empty] | 3729683 | 1846369 | 32.8 | 4727135 | 2840128 | 33.6 | 11456216 | 1430560 | 30.5 | 11550441 | 1600420 | 30.5
[12 empty] | 4465081 | 2450050 | 33 | 6083698 | 3826891 | 34 | 14009934 | 1855445 | 30.7 | 14183992 | 2089217 | 30.6
[12 empty] | 5313354 | 3012430 | 33.1 | 7050987 | 4678993 | 33.9 | 16384842 | 2253039 | 30.6 | 16574599 | 2538134 | 30.5
[12 empty] | 6209941 | 3620102 | 33.7 | 8302894 | 5603513 | 34.4 | 18936657 | 2675943 | 30.6 | 19152812 | 3017749 | 30.5
[12 empty] | 8671372 | 5180812 | 33.5 | 11039632 | 8011001 | 34.3 | 26084969 | 3782941 | 30.5 | 26384204 | 4272888 | 30.4
[12 empty] | 9480138 | 6183129 | 33.9 | 12902096 | 9568163 | 34.4 | 29924022 | 4490141 | 30.5 | 30307429 | 5082385 | 30.4
[12 empty] | 11142439 | 7378479 | 33.8 | 14657714 | 11501066 | 34.5 | 35922625 | 5355734 | 30.2 | 36339181 | 6070380 | 30.1
[12 empty] | 12737827 | 8186094 | 33.4 | 16201861 | 13106135 | 34.4 | 39789172 | 5963521 | 30.3 | 40297603 | 6751955 | 30.1
[12 empty] | 14397040 | 9805500 | 33.7 | 19432894 | 15422997 | 34.4 | 45969026 | 7134193 | 30.5 | 46559495 | 8087500 | 30.3
[12 empty] | 16439536 | 11822967 | 33.9 | 22994018 | 18429259 | 34.4 | 54472134 | 8528467 | 30.4 | 55177759 | 9664973 | 30.3
[12 empty] | 19883393 | 14427851 | 33.5 | 27505678 | 22169127 | 34.4 | 64026329 | 10161479 | 30.4 | 64860123 | 11521669 | 30.2
[12 empty] | 23296493 | 17114268 | 33.8 | 31929719 | 26479739 | 34.4 | 75505338 | 12141375 | 30.4 | 76601221 | 13780168 | 30.3
[12 empty] | 24495645 | 17684817 | 33.7 | 33405548 | 27761126 | 34.2 | 78238586 | 12605289 | 30.3 | 79335320 | 14303855 | 30.2
Mid
[12 empty] | 146562 | 7314 | 16.4 | 147349 | 9086 | 16.4 | 860329 | 43001 | 23.9 | 860706 | 43149 | 23.9
[12 empty] | 149294 | 8131 | 16.4 | 151790 | 9973 | 16.5 | 842829 | 43555 | 23.9 | 843218 | 43741 | 23.9
[12 empty] | 150179 | 9303 | 16.5 | 159851 | 10963 | 16.5 | 849854 | 43871 | 23.9 | 851214 | 44118 | 23.9
[12 empty] | 163453 | 9856 | 16.5 | 164164 | 12578 | 16.5 | 886560 | 45396 | 24 | 890364 | 45822 | 24.1
[12 empty] | 163453 | 11429 | 16.5 | 170172 | 14465 | 16.6 | 916114 | 46906 | 24.1 | 918144 | 47438 | 24.1
[12 empty] | 170069 | 12900 | 16.6 | 174511 | 16822 | 16.7 | 940622 | 47961 | 24.2 | 941211 | 48523 | 24.1
[12 empty] | 173588 | 14389 | 16.7 | 181328 | 18237 | 16.7 | 960780 | 49228 | 24.2 | 962907 | 50017 | 24.2
[12 empty] | 175657 | 16776 | 16.7 | 184748 | 21620 | 16.8 | 1017121 | 52052 | 24.4 | 1019730 | 52961 | 24.4
[12 empty] | 188562 | 18956 | 16.8 | 201406 | 26219 | 16.9 | 1084335 | 53373 | 24.2 | 1086360 | 54703 | 24.2
[12 empty] | 195823 | 22759 | 16.8 | 209789 | 32316 | 17 | 1135527 | 57999 | 24.5 | 1137462 | 59565 | 24.5
[12 empty] | 201341 | 25658 | 16.9 | 224062 | 37308 | 17.1 | 1178578 | 61568 | 24.8 | 1182425 | 63539 | 24.8
[12 empty] | 222083 | 31543 | 17.1 | 251053 | 46514 | 17.3 | 1264357 | 65678 | 24.7 | 1267678 | 68130 | 24.7
[12 empty] | 239778 | 39231 | 17.1 | 269097 | 58642 | 17.4 | 1374910 | 72224 | 24.8 | 1392859 | 74609 | 24.8
[12 empty] | 255458 | 49163 | 17.3 | 290377 | 74340 | 17.5 | 1465483 | 81171 | 25.1 | 1477114 | 85340 | 25
[12 empty] | 270368 | 56395 | 17.4 | 309201 | 85910 | 17.7 | 1596916 | 87759 | 25.1 | 1606137 | 92950 | 25.1
[12 empty] | 296767 | 72142 | 17.6 | 350308 | 111179 | 17.9 | 1766903 | 99937 | 25.1 | 1777366 | 106800 | 25.1
[12 empty] | 302990 | 76359 | 17.7 | 355039 | 117111 | 17.9 | 1775986 | 103346 | 25.1 | 1786164 | 110501 | 25.1
[12 empty] | 1020324 | 125737 | 30.1 | 1179551 | 175860 | 30.7 | 2798460 | 162610 | 30.8 | 2826031 | 170730 | 30.8
[12 empty] | 1067260 | 141173 | 30.1 | 1181128 | 196549 | 30.5 | 2872194 | 167340 | 30.6 | 2891788 | 176999 | 30.6
[12 empty] | 1113627 | 159664 | 30.1 | 1305815 | 228668 | 30.7 | 3008498 | 182369 | 30.5 | 3020853 | 192789 | 30.5
[12 empty] | 1194296 | 184729 | 30.4 | 1399450 | 266207 | 31 | 3222821 | 201683 | 30.7 | 3230735 | 214276 | 30.6
[12 empty] | 1288683 | 213836 | 30.6 | 1493002 | 309811 | 31.3 | 3391049 | 223526 | 30.6 | 3411340 | 238868 | 30.6
[12 empty] | 1348380 | 233211 | 30.6 | 1579694 | 339632 | 31.3 | 3672155 | 237571 | 30.6 | 3688563 | 254313 | 30.6
[12 empty] | 1466941 | 275623 | 31.1 | 1693947 | 399937 | 31.5 | 3933592 | 277055 | 30.7 | 3948971 | 297088 | 30.7
[12 empty] | 1567156 | 320260 | 31.2 | 1868579 | 471896 | 31.8 | 4237729 | 309698 | 30.8 | 4255401 | 333837 | 30.8
[12 empty] | 1682015 | 373190 | 31.4 | 2010990 | 553808 | 31.9 | 4706848 | 356303 | 30.9 | 4730679 | 385574 | 30.9
[12 empty] | 2034859 | 515598 | 31.7 | 2474088 | 771515 | 32.2 | 5700201 | 462952 | 30.8 | 5730630 | 504783 | 30.8
[12 empty] | 2195071 | 605085 | 31.8 | 2772450 | 909322 | 32.9 | 6242727 | 526051 | 30.9 | 6277268 | 576696 | 30.9
[12 empty] | 2475403 | 715581 | 31.9 | 3022563 | 1073022 | 32.9 | 7155265 | 618770 | 31.1 | 7202272 | 679890 | 31.1
[12 empty] | 2612288 | 771054 | 32 | 3168403 | 1157633 | 33.1 | 7393440 | 660585 | 31.1 | 7455017 | 726623 | 31
[12 empty] | 2935755 | 907009 | 32.5 | 3598453 | 1379281 | 33.2 | 8242661 | 759249 | 31 | 8302770 | 839001 | 31
[12 empty] | 3175890 | 1047970 | 32.7 | 3928470 | 1599491 | 33.4 | 9123583 | 865159 | 31.1 | 9176993 | 957169 | 31
[12 empty] | 2800416 | 1033909 | 32.3 | 3463816 | 1581705 | 33.1 | 9002597 | 864996 | 30.8 | 9053351 | 957019 | 30.8
[12 empty] | 3107798 | 1247589 | 32.4 | 4063436 | 1930435 | 33 | 9716923 | 999048 | 30.6 | 9840945 | 1117545 | 30.5
[12 empty] | 3107809 | 1247782 | 32.4 | 4063612 | 1930742 | 33 | 9717001 | 999167 | 30.6 | 9841028 | 1117684 | 30.5
[12 empty] | 3564305 | 1527999 | 32.2 | 4534850 | 2340847 | 33.3 | 11106521 | 1193873 | 30.6 | 11247173 | 1338423 | 30.5
[12 empty] | 4033068 | 1847463 | 32.8 | 5069910 | 2841685 | 33.5 | 12588985 | 1437354 | 30.5 | 12690579 | 1607482 | 30.5
[12 empty] | 4781428 | 2451440 | 33 | 6441046 | 3828830 | 33.9 | 15265417 | 1865237 | 30.7 | 15450775 | 2099690 | 30.6
[12 empty] | 5677851 | 3014277 | 33.2 | 7528215 | 4682107 | 33.8 | 17895634 | 2265936 | 30.6 | 18103968 | 2551903 | 30.5
[12 empty] | 6715644 | 3622720 | 33.6 | 8879910 | 5606642 | 34.2 | 20498253 | 2692346 | 30.6 | 20741257 | 3035257 | 30.5
[12 empty] | 9196024 | 5183916 | 33.4 | 11794994 | 8016388 | 34.1 | 28179798 | 3812443 | 30.5 | 28516222 | 4304239 | 30.5
[12 empty] | 10166335 | 6187310 | 33.7 | 13706907 | 9574885 | 34.2 | 32217723 | 4527564 | 30.5 | 32655726 | 5122709 | 30.5
[12 empty] | 11885266 | 7383573 | 33.6 | 15645119 | 11513826 | 34.2 | 38149408 | 5404573 | 30.4 | 38679017 | 6120679 | 30.3
[12 empty] | 13437931 | 8191907 | 33.4 | 17255994 | 13118945 | 34.2 | 42297994 | 6024623 | 30.4 | 42854019 | 6817651 | 30.3
[12 empty] | 15237754 | 9813644 | 33.6 | 20830352 | 15439578 | 34.1 | 49140957 | 7221853 | 30.5 | 49853529 | 8180084 | 30.4
[12 empty] | 18220942 | 11786793 | 33.5 | 24529564 | 18450394 | 34.1 | 57904101 | 8640909 | 30.5 | 58677342 | 9783601 | 30.4
[12 empty] | 21022314 | 14443723 | 33.4 | 29133864 | 22196176 | 34.2 | 68027840 | 10295408 | 30.5 | 68935550 | 11661124 | 30.4
[12 empty] | 24892803 | 17144204 | 33.6 | 34068253 | 26522120 | 34.1 | 80252740 | 12298818 | 30.5 | 81507529 | 13944806 | 30.4
[12 empty] | 26164416 | 17717685 | 33.6 | 35500824 | 27804669 | 34 | 83167964 | 12767638 | 30.4 | 84421770 | 14473107 | 30.3
High
[12 empty] | 197116 | 7360 | 18.8 | 198068 | 9137 | 18.8 | 1095210 | 47186 | 27 | 1095310 | 47337 | 27
[12 empty] | 200465 | 8177 | 18.9 | 203796 | 10029 | 18.9 | 1072874 | 48016 | 27.1 | 1073000 | 48202 | 27.1
[12 empty] | 201565 | 9356 | 18.9 | 214220 | 11026 | 19 | 1088648 | 48208 | 27.2 | 1089818 | 48455 | 27.2
[12 empty] | 221293 | 9918 | 19.1 | 222431 | 12644 | 19.1 | 1158974 | 49832 | 27.5 | 1163226 | 50267 | 27.5
[12 empty] | 221300 | 11492 | 19.1 | 230990 | 14540 | 19.2 | 1214285 | 51414 | 27.6 | 1216611 | 51955 | 27.6
[12 empty] | 230531 | 12969 | 19.1 | 237057 | 16901 | 19.2 | 1259378 | 52495 | 27.7 | 1259720 | 53057 | 27.7
[12 empty] | 238545 | 14464 | 19.2 | 250729 | 18325 | 19.3 | 1298307 | 53794 | 27.8 | 1300777 | 54591 | 27.8
[12 empty] | 241821 | 16857 | 19.2 | 255950 | 21717 | 19.3 | 1409288 | 56746 | 27.9 | 1411857 | 57654 | 28
[12 empty] | 264896 | 19048 | 19.4 | 281731 | 26327 | 19.5 | 1493310 | 58044 | 27.7 | 1495689 | 59385 | 27.7
[12 empty] | 274090 | 22862 | 19.4 | 294233 | 32444 | 19.6 | 1601730 | 62781 | 28.1 | 1603649 | 64347 | 28.1
[12 empty] | 281724 | 25765 | 19.5 | 324861 | 37455 | 20 | 1699595 | 66793 | 28.4 | 1704030 | 68774 | 28.5
[12 empty] | 322203 | 31671 | 19.6 | 374739 | 46682 | 20.1 | 1835964 | 70815 | 28.3 | 1839520 | 73266 | 28.3
[12 empty] | 357730 | 39378 | 20 | 401623 | 58834 | 20.2 | 2039097 | 77519 | 28.4 | 2053069 | 79803 | 28.2
[12 empty] | 381657 | 49338 | 20.2 | 433262 | 74564 | 20.4 | 2217717 | 86530 | 28.6 | 2226071 | 90889 | 28.7
[12 empty] | 421505 | 56580 | 20.2 | 478105 | 86158 | 20.5 | 2426059 | 93628 | 28.7 | 2437092 | 98842 | 28.7
[12 empty] | 458518 | 72364 | 20.4 | 547437 | 111499 | 20.7 | 2745920 | 106097 | 28.6 | 2759030 | 112987 | 28.6
[12 empty] | 471119 | 76603 | 20.5 | 552695 | 117433 | 20.7 | 2783070 | 109612 | 28.6 | 2795589 | 116781 | 28.7
[12 empty] | 1514327 | 126079 | 33.1 | 1764062 | 176321 | 33.7 | 3966031 | 163953 | 33.3 | 4015566 | 172109 | 33.4
[12 empty] | 1588955 | 141519 | 33.1 | 1770171 | 196966 | 33.6 | 3957144 | 168601 | 33 | 3983516 | 178304 | 33
[12 empty] | 1710001 | 160015 | 33 | 1996806 | 229151 | 33.6 | 4227787 | 183704 | 33 | 4243623 | 194135 | 33
[12 empty] | 1826278 | 185140 | 33.3 | 2129784 | 266755 | 33.8 | 4554880 | 203210 | 33.1 | 4567139 | 215823 | 33.1
[12 empty] | 1966567 | 214302 | 33.5 | 2262336 | 310422 | 34 | 4824832 | 225144 | 33.2 | 4851327 | 240513 | 33.2
[12 empty] | 2053523 | 233689 | 33.5 | 2379584 | 340260 | 34 | 5224297 | 239326 | 33.1 | 5246255 | 256084 | 33.1
[12 empty] | 2218921 | 276206 | 33.8 | 2564864 | 400653 | 34.2 | 5570139 | 279039 | 33.1 | 5591364 | 299089 | 33.1
[12 empty] | 2370064 | 320903 | 34 | 2824978 | 472736 | 34.4 | 6032833 | 311955 | 33.2 | 6057645 | 336124 | 33.2
[12 empty] | 2525026 | 373893 | 34.1 | 3018134 | 554728 | 34.5 | 6797031 | 359153 | 33.3 | 6830473 | 388472 | 33.3
[12 empty] | 3113390 | 516505 | 34.1 | 3759714 | 772714 | 34.6 | 8343067 | 466558 | 33.2 | 8386631 | 508438 | 33.3
[12 empty] | 3342122 | 606090 | 34.3 | 4176905 | 916954 | 34.7 | 9151441 | 530174 | 33.2 | 9210955 | 580902 | 33.3
[12 empty] | 3686979 | 716746 | 34.5 | 4518011 | 1082312 | 34.9 | 10593424 | 624413 | 33.4 | 10629633 | 688145 | 33.4
[12 empty] | 3904247 | 772336 | 34.5 | 4728457 | 1167413 | 35 | 10940993 | 665999 | 33.4 | 11039196 | 732174 | 33.5
[12 empty] | 4364125 | 914643 | 34.4 | 5263165 | 1389746 | 34.9 | 12274269 | 765555 | 33.5 | 12365824 | 845504 | 33.5
[12 empty] | 4775385 | 1058497 | 34.6 | 5747796 | 1610398 | 35.1 | 13698433 | 872624 | 33.5 | 13785707 | 964808 | 33.5
[12 empty] | 4222493 | 1044049 | 34.1 | 5088034 | 1592040 | 34.6 | 13371066 | 872465 | 33.2 | 13454242 | 964664 | 33.2
[12 empty] | 4627434 | 1258183 | 34.2 | 6002358 | 1938682 | 34.4 | 14495285 | 1007195 | 33 | 14665495 | 1126296 | 33.1
[12 empty] | 4627447 | 1258376 | 34.2 | 6002372 | 1938989 | 34.4 | 14495381 | 1007314 | 33 | 14665600 | 1126435 | 33.1
[12 empty] | 5230391 | 1530002 | 34.1 | 6709917 | 2351515 | 34.6 | 16767711 | 1211009 | 33 | 16962627 | 1356208 | 33
[12 empty] | 6149024 | 1856236 | 34 | 7675666 | 2853698 | 34.6 | 19358699 | 1450942 | 33 | 19523830 | 1621607 | 33.1
[12 empty] | 7227401 | 2462647 | 34.2 | 9870606 | 3839798 | 35 | 23638581 | 1884821 | 33.1 | 23636343 | 2120637 | 33.1
[12 empty] | 8571231 | 3029751 | 34.4 | 11397312 | 4699614 | 34.8 | 27512315 | 2291729 | 33 | 27816179 | 2579441 | 33
[12 empty] | 10268934 | 3637735 | 34.6 | 13694323 | 5624905 | 35.2 | 31851278 | 2725152 | 33.1 | 32212194 | 3070272 | 33.1
[12 empty] | 13831944 | 5200564 | 34.8 | 18296349 | 8028338 | 34.9 | 44071995 | 3873036 | 33 | 44631353 | 4366942 | 33.1
[12 empty] | 15736981 | 6203560 | 34.8 | 20806682 | 9599728 | 35.1 | 50805066 | 4602410 | 33 | 51442665 | 5203358 | 33.1
[12 empty] | 18117843 | 7403001 | 34.6 | 23940619 | 11539347 | 34.9 | 60242255 | 5502250 | 32.9 | 60925529 | 6231363 | 32.9
[12 empty] | 20141170 | 8214826 | 34.7 | 27094020 | 13144564 | 35.1 | 66937221 | 6146828 | 32.9 | 67784356 | 6949042 | 32.9
[12 empty] | 23597897 | 9839475 | 34.6 | 32214912 | 15472740 | 35 | 77652391 | 7390715 | 32.9 | 78641577 | 8362809 | 33
[12 empty] | 26891047 | 11821470 | 34.7 | 37887803 | 18492664 | 35 | 91436631 | 8865792 | 32.9 | 92569202 | 10020858 | 33
[12 empty] | 33107489 | 14475465 | 34.5 | 43628166 | 22366806 | 35.1 | 108658487 | 10563268 | 33 | 110037279 | 11940033 | 33
[12 empty] | 37999638 | 17204075 | 34.5 | 53772983 | 27182263 | 34.9 | 128437987 | 12613703 | 33 | 130256573 | 14274082 | 33
[12 empty] | 39899905 | 17783421 | 34.5 | 54980699 | 28044043 | 34.8 | 133199429 | 13092335 | 33 | 135028205 | 14811611 | 33