## Sheet1
Table 3. Example values for key WBS model inputs for nitrate removal
Technology | Input | Value Selected to Generate Example Costs
|  | Influent concentration 90 mg/L as nitrate | Influent concentration 195 mg/L as nitrate
Anion Exchange | Resin type | Nitrate-selective | Nitrate-selective
| Number of bed volumes before regeneration | 420 | 260
| Vessel configuration | Parallel | Parallel
| Empty bed contact time | 2 minutes | 3 minutes
| Discharge option for spent brine | Publicly owned treatment works | Publicly owned treatment works
Biological Treatment | Design type | Fluidized bed | Fluidized bed
| Electron donor requirements | 28.5 mg/L acetic acid | 40.6 mg/L acetic acid
| Biomass generation | 11.3 mg/L | 14.9 mg/L
| Nutrient requirements | 2 mg/L phosphoric acid (as phosphorus) | 2 mg/L phosphoric acid (as phosphorus)
| Empty bed contact time | 10 minutes | 10 minutes
| Post-treatment options | Aeration and polishing filter | Aeration and polishing filter
| Discharge option for spent backwash | Recycle | Recycle
POU/POE Treatment | Technology | POU reverse osmosis (purchased) | POU reverse osmosis (purchased)
| Water source | Groundwater | Groundwater
| Include UV disinfection | No | No
WBS – work breakdown structure; POU/POE – point-of-use/point-of entry; POU – point-of-use; UV – ultraviolet

## Data
| Discount Rate | 3%
| Component Level | low
|  | Annualized Costs ($2017) | [5 empty] | $/kgal | [5 empty] | AX - LO |  |  | AX - HI |  |  | BIO - LO |  |  | BIO - HI |  |  | BIO FXB - HI |  |  | POU
Average Flow (MGD) | Design Flow (MGD) | Anion exchange - lower influent nitrate | Anion exchange - higher influent nitrate | Biological treatment - lower influent nitrate | Biological fluidized bed treatment - higher influent nitrate | Biological fixed bed treatment - higher influent nitrate | POU reverse osmosis | Anion exchange - lower influent nitrate | Anion exchange - higher influent nitrate | Biological treatment - lower influent nitrate | Biological treatment - higher influent nitrate | Biological fixed bed treatment - higher influent nitrate | POU reverse osmosis | TC | OM | UL | TC | OM | UL | TC | OM | UL | TC | OM | UL | TC | OM | UL | TC | OM | UL
0.007 | 0.03 | 15605.1654 | 17440.1983 | 76918.0924 | 77075.1437 | 63951.0055 | 7637.6056 | 6.1077 | 6.8259 | 30.1049 | 30.1664 | 25.0297 | 2.9893 | 103125 | 7314 | 15.8 | 103909 | 9086 | 15.8 | 671104 | 37627 | 24.3 | 671344 | 37770 | 24.3 | 483471 | 28193 | 17.6 | 11538 | 6285 | 10
0.009 | 0.038 | 16500.1526 | 18498.6094 | 76764.5631 | 76966.3265 | 64022.6309 | 9167.9808 | 5.0229 | 5.6312 | 23.3682 | 23.4296 | 19.4894 | 2.7909 | 104095 | 8131 | 15.8 | 106041 | 9973 | 15.8 | 667002 | 37823 | 24.4 | 667272 | 38009 | 24.4 | 480845 | 28612 | 17.7 | 14450 | 7474 | 10
0.012 | 0.049 | 17742.9039 | 19910.1449 | 78183.062 | 78502.2817 | 65502.7906 | 11361.5425 | 4.0509 | 4.5457 | 17.85 | 17.9229 | 14.955 | 2.594 | 104975 | 9303 | 15.8 | 112386 | 10963 | 16 | 683094 | 38302 | 24.4 | 684331 | 38549 | 24.4 | 492919 | 29203 | 17.7 | 18609 | 9180 | 10
0.016 | 0.063 | 18925.7456 | 21736.5117 | 81508.841 | 82122.5472 | 68528.322 | 14209.5251 | 3.2407 | 3.722 | 13.957 | 14.0621 | 11.7343 | 2.4331 | 113926 | 9856 | 16 | 115041 | 12578 | 16 | 717993 | 39707 | 24.5 | 721406 | 40122 | 24.5 | 516508 | 30654 | 17.8 | 24017 | 11394 | 10
0.022 | 0.081 | 20498.7456 | 24053.659 | 83632.3574 | 84247.1945 | 71413.2279 | 17941.5792 | 2.5528 | 2.9955 | 10.415 | 10.4916 | 8.8933 | 2.2343 | 113926 | 11429 | 16 | 121032 | 14465 | 16.1 | 740065 | 41132 | 25 | 741699 | 41653 | 25 | 538882 | 32066 | 17.9 | 31089 | 14297 | 10
0.028 | 0.103 | 22235.8546 | 26614.061 | 85824.7511 | 86412.7085 | 75941.4826 | 22324.8198 | 2.1757 | 2.6041 | 8.3977 | 8.4553 | 7.4307 | 2.1844 | 117841 | 12900 | 16.1 | 124198 | 16822 | 16.2 | 760393 | 42157 | 25 | 760845 | 42719 | 25 | 589900 | 33583 | 18.3 | 39408 | 17705 | 10
0.035 | 0.124 | 24046.3983 | 28540.5128 | 88243.487 | 89123.1999 | 73599.4634 | 26714.1776 | 1.8823 | 2.2341 | 6.9075 | 6.9764 | 5.7612 | 2.0911 | 122490 | 14389 | 16.2 | 131313 | 18237 | 16.3 | 783148 | 43390 | 25.1 | 784889 | 44170 | 25.1 | 644202 | 35561 | 24 | 47728 | 21119 | 10
0.046 | 0.159 | 26694.7607 | 32288.6655 | 92760.6049 | 93809.1515 | 74799.9085 | 33954.4008 | 1.5899 | 1.9231 | 5.5248 | 5.5872 | 4.455 | 2.0223 | 125805 | 16776 | 16.2 | 136615 | 21620 | 16.4 | 826168 | 46066 | 25.6 | 828637 | 46975 | 25.6 | 643482 | 37126 | 24.3 | 61455 | 26750 | 10
0.06 | 0.203 | 29556.7246 | 37779.0641 | 96805.8218 | 98193.0692 | 78936.3185 | 43152.6522 | 1.3496 | 1.7251 | 4.4204 | 4.4837 | 3.6044 | 1.9704 | 135745 | 18956 | 16.4 | 148730 | 26219 | 16.5 | 864604 | 48066 | 25.7 | 866471 | 49348 | 25.7 | 669293 | 39861 | 24.4 | 78927 | 33900 | 10
0.079 | 0.26 | 33928.8837 | 44676.2104 | 103404.5577 | 105077.674 | 86377.7222 | 55232.769 | 1.1767 | 1.5494 | 3.5861 | 3.6441 | 2.9956 | 1.9155 | 143710 | 22759 | 16.5 | 161258 | 32316 | 16.8 | 916510 | 52005 | 25.9 | 918420 | 53571 | 25.9 | 719106 | 44627 | 24.6 | 101806 | 43298 | 10
0.094 | 0.305 | 37218.0641 | 50710.9751 | 108448.1433 | 110599.5082 | 90636.7366 | 65109.2068 | 1.0848 | 1.478 | 3.1608 | 3.2235 | 2.6417 | 1.8977 | 148730 | 25658 | 16.5 | 175665 | 37308 | 16.9 | 956360 | 54951 | 26 | 959781 | 56911 | 26 | 755813 | 46633 | 24.5 | 120525 | 50980 | 10
0.123 | 0.39 | 44336.2754 | 61417.5861 | 116477.9516 | 119254.3387 | 99964.699 | 83526.4752 | 0.98755 | 1.368 | 2.5945 | 2.6563 | 2.2266 | 1.8605 | 166908 | 31543 | 16.8 | 197994 | 46514 | 17.2 | 1021239 | 59205 | 25.9 | 1024380 | 61657 | 25.8 | 808383 | 53415 | 24.9 | 155467 | 65301 | 10
0.162 | 0.5 | 53203.9109 | 74972.1356 | 128294.5613 | 132069.2709 | 111210.75 | 107655.7087 | 0.89978 | 1.2679 | 2.1697 | 2.2335 | 1.8808 | 1.8207 | 183969 | 39231 | 17 | 217912 | 58642 | 17.3 | 1118144 | 65587 | 25.9 | 1124665 | 68996 | 25.9 | 884065 | 60303 | 24.9 | 201225 | 84066 | 10
0.213 | 0.64 | 64585.2918 | 90887.8126 | 140875.1424 | 145866.8738 | 125931.6676 | 138565.6296 | 0.83073 | 1.1691 | 1.812 | 1.8762 | 1.6198 | 1.7823 | 204885 | 49163 | 17.2 | 230451 | 74340 | 18.3 | 1197728 | 74216 | 26.2 | 1207911 | 78641 | 26.2 | 965557 | 70779 | 25.2 | 259878 | 108100 | 10
0.25 | 0.74 | 72815.3624 | 103618.1777 | 151311.9392 | 157128.5807 | 136915.8701 | 161208.4879 | 0.79798 | 1.1355 | 1.6582 | 1.722 | 1.5004 | 1.7667 | 219116 | 56395 | 17.3 | 247625 | 85910 | 18.4 | 1276043 | 80473 | 26.3 | 1284557 | 85637 | 26.2 | 1039370 | 77547 | 25.2 | 302724 | 125720 | 10
0.329 | 0.947 | 89028.0199 | 131132.8948 | 172060.2136 | 179425.7784 | 157035.0458 | 207933.5797 | 0.74138 | 1.092 | 1.4328 | 1.4942 | 1.3077 | 1.7316 | 235161 | 72142 | 18.3 | 282437 | 111179 | 18.7 | 1432211 | 92351 | 26.2 | 1441834 | 99181 | 26.2 | 1146936 | 91522 | 25.2 | 391328 | 162058 | 10
0.349 | 0.999 | 93618.94 | 137398.8527 | 175666.4311 | 183541.4188 | 164625.0463 | 219743.9286 | 0.73493 | 1.0786 | 1.379 | 1.4408 | 1.2923 | 1.725 | 241357 | 76359 | 18.4 | 287164 | 117111 | 18.7 | 1441486 | 95643 | 26.3 | 1451099 | 102781 | 26.2 | 1202909 | 96279 | 25.4 | 413791 | 171235 | 10
0.35 | 1 | 166992.1033 | 224254.2971 | 270415.2747 | 279469.647 | 274036.8428 |  | 1.3072 | 1.7554 | 2.1168 | 2.1876 | 2.1451 |  | 876498 | 121993 | 29.7 | 1038096 | 171617 | 30.3 | 2438636 | 149667 | 31.5 | 2459607 | 157683 | 31.5 | 2430872 | 153673 | 31.5
0.42 | 1.181 | 184384.8698 | 243152.0012 | 278823.4181 | 289249.7892 | 284347.1597 |  | 1.2028 | 1.5861 | 1.8188 | 1.8868 | 1.8548 |  | 921410 | 137080 | 29.7 | 1025742 | 191866 | 31 | 2421528 | 158458 | 31.3 | 2438656 | 168033 | 31.3 | 2464081 | 162805 | 31.7
0.505 | 1.394 | 205197.4984 | 279623.0563 | 299890.7158 | 310852.1241 | 309566.4916 |  | 1.1132 | 1.517 | 1.627 | 1.6864 | 1.6795 |  | 973721 | 155207 | 29.7 | 1125169 | 223586 | 31.2 | 2544327 | 173175 | 31.2 | 2555720 | 183569 | 31.2 | 2633432 | 179671 | 31.7
0.607 | 1.645 | 231916.8493 | 320675.0024 | 327429.5664 | 340607.6462 | 339280.6577 |  | 1.0468 | 1.4474 | 1.4779 | 1.5374 | 1.5314 |  | 1033996 | 180013 | 30.8 | 1210530 | 260736 | 31.5 | 2733078 | 191841 | 31.4 | 2740224 | 204401 | 31.3 | 2802658 | 201038 | 31.7
0.729 | 1.941 | 264164.5184 | 368936.0721 | 357789.6297 | 374005.996 | 377643.2786 |  | 0.99278 | 1.3865 | 1.3446 | 1.4056 | 1.4193 |  | 1110595 | 208745 | 31.1 | 1317270 | 303961 | 31.7 | 2906872 | 213018 | 31.2 | 2925593 | 228302 | 31.2 | 3016182 | 228298 | 31.5
0.817 | 2.152 | 285610.0593 | 401452.708 | 379670.7428 | 397471.624 | 402335.6407 |  | 0.95776 | 1.3462 | 1.2732 | 1.3329 | 1.3492 |  | 1158040 | 227823 | 31.1 | 1381211 | 333453 | 31.8 | 3075716 | 226788 | 31.3 | 3091639 | 243498 | 31.2 | 3181046 | 245129 | 31.6
0.981 | 2.539 | 333239.7914 | 466447.0831 | 431061.3751 | 451835.3153 | 459398.4391 |  | 0.93067 | 1.3027 | 1.2039 | 1.2619 | 1.283 |  | 1284524 | 269637 | 31.5 | 1491970 | 393271 | 32 | 3331048 | 265487 | 31.3 | 3346578 | 285489 | 31.3 | 3479463 | 287772 | 31.7
1.179 | 2.996 | 381808.6339 | 545235.4296 | 475331.0769 | 500862.6677 | 513236.235 |  | 0.88724 | 1.267 | 1.1046 | 1.1639 | 1.1926 |  | 1375231 | 313845 | 31.6 | 1650504 | 464735 | 32.3 | 3586582 | 297400 | 31.4 | 3608483 | 321498 | 31.3 | 3741461 | 328334 | 31.6
1.417 | 3.536 | 439096.7914 | 633531.5921 | 544411.323 | 575335.5762 | 578718.7706 |  | 0.84898 | 1.2249 | 1.0526 | 1.1124 | 1.1189 |  | 1481610 | 366292 | 31.9 | 1796366 | 545917 | 32.3 | 4067617 | 342616 | 31.4 | 4094475 | 371814 | 31.3 | 4103513 | 375924 | 31.6
2.044 | 4.923 | 594633.7362 | 868369.1726 | 689210.0486 | 732383.9428 | 746050.0508 |  | 0.79703 | 1.1639 | 0.9238 | 0.98167 | 0.99999 |  | 1788090 | 507098 | 32.1 | 2196466 | 761829 | 32.6 | 4877656 | 446287 | 31.2 | 4906146 | 488042 | 31.2 | 5027703 | 497582 | 31.6
2.455 | 5.809 | 691213.6824 | 1017587.329 | 774531.6834 | 827534.8163 | 856831.7322 |  | 0.77138 | 1.1356 | 0.86436 | 0.92351 | 0.95621 |  | 1951890 | 595837 | 32.2 | 2478195 | 899090 | 33.4 | 5372900 | 507981 | 31.4 | 5412419 | 558503 | 31.3 | 5641742 | 578018 | 31.6
2.949 | 6.855 | 812418.0861 | 1191510.5873 | 903072.8444 | 966966.1918 | 982518.3552 |  | 0.75477 | 1.107 | 0.83899 | 0.89835 | 0.91279 |  | 2196042 | 705310 | 32.3 | 2713812 | 1061747 | 33.4 | 6230892 | 593957 | 31.4 | 6278110 | 654904 | 31.3 | 6348435 | 668780 | 31.6
3.193 | 7.365 | 872994.1545 | 1281776.6029 | 955903.7122 | 1024242.4091 | 1036779.1381 |  | 0.74907 | 1.0998 | 0.8202 | 0.87884 | 0.8896 |  | 2312828 | 760398 | 32.4 | 2854206 | 1145776 | 33.6 | 6473709 | 634119 | 31.3 | 6523616 | 699977 | 31.3 | 6576315 | 711779 | 31.6
3.836 | 8.691 | 1022679.1828 | 1521617.5706 | 1093850.6704 | 1176236.3808 | 1194946.7356 |  | 0.73041 | 1.0868 | 0.78124 | 0.84008 | 0.85345 |  | 2639603 | 895338 | 32.9 | 3261073 | 1365959 | 33.5 | 7218039 | 735068 | 31.3 | 7276074 | 814569 | 31.3 | 7331235 | 831943 | 31.5
4.481 | 9.999 | 1173079.8764 | 1754931.3749 | 1235800.9775 | 1328331.5331 | 1338279.8735 |  | 0.71723 | 1.073 | 0.75558 | 0.81215 | 0.81824 |  | 2862458 | 1035235 | 33 | 3577960 | 1584740 | 33.7 | 8015346 | 838158 | 31.4 | 8014634 | 929953 | 31.3 | 7970933 | 944358 | 31.6
4.481 | 10 | 1156623.9813 | 1732304.9829 | 1262971.9454 | 1357254.9287 | 1353888.8586 |  | 0.70717 | 1.0591 | 0.77219 | 0.82984 | 0.82778 |  | 2526877 | 1033380 | 32.3 | 3154218 | 1580950 | 33.2 | 8018536 | 861261 | 30.9 | 8065404 | 953196 | 30.9 | 7825794 | 964139 | 31.2
5.484 | 12 | 1383674.7776 | 2104569.6534 | 1429781.5041 | 1554516.425 | 1554154.986 |  | 0.69126 | 1.0514 | 0.7143 | 0.77661 | 0.77643 |  | 2813141 | 1246973 | 32.5 | 3652284 | 1929315 | 33.2 | 8644680 | 994975 | 30.7 | 8757130 | 1113170 | 30.6 | 8546604 | 1125989 | 30.9
5.485 | 12.001 | 1383868.3607 | 2104877.2772 | 1429909.5636 | 1554658.5577 | 1554292.2924 |  | 0.69123 | 1.0514 | 0.71423 | 0.77654 | 0.77636 |  | 2813153 | 1247166 | 32.5 | 3652297 | 1929622 | 33.2 | 8644880 | 995093 | 30.7 | 8757212 | 1113308 | 30.6 | 8546670 | 1126123 | 30.9
6.712 | 14.401 | 1681785.0508 | 2535692.7808 | 1686702.1597 | 1838257.8494 | 1848039.3232 |  | 0.68648 | 1.035 | 0.68848 | 0.75035 | 0.75434 |  | 3173606 | 1526998 | 32.3 | 4109203 | 2339551 | 33.5 | 9903342 | 1188588 | 30.7 | 10030390 | 1332741 | 30.6 | 9931562 | 1350490 | 30.9
8.215 | 17.282 | 2026622.8955 | 3065372.1519 | 2009100.8775 | 2183719.2562 | 2185693.3258 |  | 0.67588 | 1.0223 | 0.67004 | 0.72828 | 0.72893 |  | 3729683 | 1846369 | 32.8 | 4727135 | 2840128 | 33.6 | 11456216 | 1430560 | 30.5 | 11550441 | 1600420 | 30.5 | 11500556 | 1608396 | 30.8
11.066 | 22.614 | 2665070.9849 | 4114783.5336 | 2560110.8089 | 2804069.2588 | 2843654.3894 |  | 0.65982 | 1.0187 | 0.63383 | 0.69423 | 0.70403 |  | 4465081 | 2450050 | 33 | 6083698 | 3826891 | 34 | 14009934 | 1855445 | 30.7 | 14183992 | 2089217 | 30.6 | 14324232 | 2126042 | 30.9
13.543 | 27.137 | 3267844.2842 | 5013230.8431 | 3078810.85 | 3375154.0989 | 3441044.8601 |  | 0.66108 | 1.0142 | 0.62284 | 0.68279 | 0.69612 |  | 5313354 | 3012430 | 33.1 | 7050987 | 4678993 | 33.9 | 16384842 | 2253039 | 30.6 | 16574599 | 2538134 | 30.5 | 16972422 | 2590764 | 30.9
16.282 | 32.564 | 3915487.7496 | 5993773.6686 | 3630322.5591 | 3984969.2986 | 4036879.8734 |  | 0.65885 | 1.0086 | 0.61086 | 0.67054 | 0.67927 |  | 6209941 | 3620102 | 33.7 | 8302894 | 5603513 | 34.4 | 18936657 | 2675943 | 30.6 | 19152812 | 3017749 | 30.5 | 19395413 | 3067130 | 31
23.446 | 46.892 | 5594716.6783 | 8530768.53 | 5100236.4189 | 5607995.569 | 5746443.8774 |  | 0.65376 | 0.99684 | 0.59598 | 0.65531 | 0.67149 |  | 8671372 | 5180812 | 33.5 | 11039632 | 8011001 | 34.3 | 26084969 | 3782941 | 30.5 | 26384204 | 4272888 | 30.4 | 27430047 | 4364010 | 30.6
28.136 | 56.271 | 6632515.8556 | 10174599.8173 | 6001309.2553 | 6616017.6938 | 6832986.7261 |  | 0.64584 | 0.99075 | 0.58437 | 0.64423 | 0.66536 |  | 9480138 | 6183129 | 33.9 | 12902096 | 9568163 | 34.4 | 29924022 | 4490141 | 30.5 | 30307429 | 5082385 | 30.4 | 31960318 | 5225460 | 30.7
33.762 | 67.525 | 7907572.4691 | 12188871.5023 | 7180941.9614 | 7920552.0247 | 8275113.0177 |  | 0.64169 | 0.98911 | 0.58272 | 0.64274 | 0.67151 |  | 11142439 | 7378479 | 33.8 | 14657714 | 11501066 | 34.5 | 35922625 | 5355734 | 30.2 | 36339181 | 6070380 | 30.1 | 39006071 | 6301307 | 30.4
37.536 | 75.072 | 8795165.714 | 13867670.569 | 7981055.4735 | 8803666.0095 | 8966698.6215 |  | 0.64195 | 1.0122 | 0.58253 | 0.64257 | 0.65447 |  | 12737827 | 8186094 | 33.4 | 16201861 | 13106135 | 34.4 | 39789172 | 5963521 | 30.3 | 40297603 | 6751955 | 30.1 | 40780175 | 6911438 | 30.6
45.043 | 90.086 | 10490318.1735 | 16336400.7127 | 9455636.7157 | 10448327.8713 | 10626105.6333 |  | 0.63807 | 0.99366 | 0.57514 | 0.63552 | 0.64633 |  | 14397040 | 9805500 | 33.7 | 19432894 | 15422997 | 34.4 | 45969026 | 7134193 | 30.5 | 46559495 | 8087500 | 30.3 | 47258074 | 8253876 | 30.8
54.052 | 108.104 | 12602250.1065 | 19510046.1134 | 11284894.9901 | 12462795.2556 | 13052388.997 |  | 0.63877 | 0.9889 | 0.572 | 0.6317 | 0.66158 |  | 16439536 | 11822967 | 33.9 | 22994018 | 18429259 | 34.4 | 54472134 | 8528467 | 30.4 | 55177759 | 9664973 | 30.3 | 59411998 | 10058112 | 30.6
64.862 | 129.724 | 15376931.4203 | 23461975.5281 | 13401373.4634 | 14817174.6284 | 15482853.6222 |  | 0.64951 | 0.99102 | 0.56606 | 0.62587 | 0.65399 |  | 19883393 | 14427851 | 33.5 | 27505678 | 22169127 | 34.4 | 64026329 | 10161479 | 30.4 | 64860123 | 11521669 | 30.2 | 69419776 | 11977143 | 30.5
77.834 | 155.669 | 18220491.0002 | 27980530.5897 | 15962136.4019 | 17664280.0917 | 18444913.6154 |  | 0.64135 | 0.9849 | 0.56186 | 0.62178 | 0.64925 |  | 23296493 | 17114268 | 33.8 | 31929719 | 26479739 | 34.4 | 75505338 | 12141375 | 30.4 | 76601221 | 13780168 | 30.3 | 81630764 | 14322546 | 30.5
81 | 162 | 18849991.4294 | 29336580.258 | 16572424.6925 | 18334837.0811 | 19196657.0267 |  | 0.63758 | 0.99227 | 0.56054 | 0.62015 | 0.6493 |  | 24495645 | 17684817 | 33.7 | 33405548 | 27761126 | 34.2 | 78238586 | 12605289 | 30.3 | 79335320 | 14303855 | 30.2 | 85122186 | 14897972 | 30.5
Low
[14 empty] | 103125 | 7314 | 15.8 | 103909 | 9086 | 15.8 | 671104 | 37627 | 24.3 | 671344 | 37770 | 24.3 | 483471 | 28193 | 17.6
[14 empty] | 104095 | 8131 | 15.8 | 106041 | 9973 | 15.8 | 667002 | 37823 | 24.4 | 667272 | 38009 | 24.4 | 480845 | 28612 | 17.7
[14 empty] | 104975 | 9303 | 15.8 | 112386 | 10963 | 16 | 683094 | 38302 | 24.4 | 684331 | 38549 | 24.4 | 492919 | 29203 | 17.7
[14 empty] | 113926 | 9856 | 16 | 115041 | 12578 | 16 | 717993 | 39707 | 24.5 | 721406 | 40122 | 24.5 | 516508 | 30654 | 17.8
[14 empty] | 113926 | 11429 | 16 | 121032 | 14465 | 16.1 | 740065 | 41132 | 25 | 741699 | 41653 | 25 | 538882 | 32066 | 17.9
[14 empty] | 117841 | 12900 | 16.1 | 124198 | 16822 | 16.2 | 760393 | 42157 | 25 | 760845 | 42719 | 25 | 589900 | 33583 | 18.3
[14 empty] | 122490 | 14389 | 16.2 | 131313 | 18237 | 16.3 | 783148 | 43390 | 25.1 | 784889 | 44170 | 25.1 | 644202 | 35561 | 24
[14 empty] | 125805 | 16776 | 16.2 | 136615 | 21620 | 16.4 | 826168 | 46066 | 25.6 | 828637 | 46975 | 25.6 | 643482 | 37126 | 24.3
[14 empty] | 135745 | 18956 | 16.4 | 148730 | 26219 | 16.5 | 864604 | 48066 | 25.7 | 866471 | 49348 | 25.7 | 669293 | 39861 | 24.4
[14 empty] | 143710 | 22759 | 16.5 | 161258 | 32316 | 16.8 | 916510 | 52005 | 25.9 | 918420 | 53571 | 25.9 | 719106 | 44627 | 24.6
[14 empty] | 148730 | 25658 | 16.5 | 175665 | 37308 | 16.9 | 956360 | 54951 | 26 | 959781 | 56911 | 26 | 755813 | 46633 | 24.5
[14 empty] | 166908 | 31543 | 16.8 | 197994 | 46514 | 17.2 | 1021239 | 59205 | 25.9 | 1024380 | 61657 | 25.8 | 808383 | 53415 | 24.9
[14 empty] | 183969 | 39231 | 17 | 217912 | 58642 | 17.3 | 1118144 | 65587 | 25.9 | 1124665 | 68996 | 25.9 | 884065 | 60303 | 24.9
[14 empty] | 204885 | 49163 | 17.2 | 230451 | 74340 | 18.3 | 1197728 | 74216 | 26.2 | 1207911 | 78641 | 26.2 | 965557 | 70779 | 25.2
[14 empty] | 219116 | 56395 | 17.3 | 247625 | 85910 | 18.4 | 1276043 | 80473 | 26.3 | 1284557 | 85637 | 26.2 | 1039370 | 77547 | 25.2
[14 empty] | 235161 | 72142 | 18.3 | 282437 | 111179 | 18.7 | 1432211 | 92351 | 26.2 | 1441834 | 99181 | 26.2 | 1146936 | 91522 | 25.2
[14 empty] | 241357 | 76359 | 18.4 | 287164 | 117111 | 18.7 | 1441486 | 95643 | 26.3 | 1451099 | 102781 | 26.2 | 1202909 | 96279 | 25.4
[14 empty] | 876498 | 121993 | 29.7 | 1038096 | 171617 | 30.3 | 2438636 | 149667 | 31.5 | 2459607 | 157683 | 31.5 | 2430872 | 153673 | 31.5
[14 empty] | 921410 | 137080 | 29.7 | 1025742 | 191866 | 31 | 2421528 | 158458 | 31.3 | 2438656 | 168033 | 31.3 | 2464081 | 162805 | 31.7
[14 empty] | 973721 | 155207 | 29.7 | 1125169 | 223586 | 31.2 | 2544327 | 173175 | 31.2 | 2555720 | 183569 | 31.2 | 2633432 | 179671 | 31.7
[14 empty] | 1033996 | 180013 | 30.8 | 1210530 | 260736 | 31.5 | 2733078 | 191841 | 31.4 | 2740224 | 204401 | 31.3 | 2802658 | 201038 | 31.7
[14 empty] | 1110595 | 208745 | 31.1 | 1317270 | 303961 | 31.7 | 2906872 | 213018 | 31.2 | 2925593 | 228302 | 31.2 | 3016182 | 228298 | 31.5
[14 empty] | 1158040 | 227823 | 31.1 | 1381211 | 333453 | 31.8 | 3075716 | 226788 | 31.3 | 3091639 | 243498 | 31.2 | 3181046 | 245129 | 31.6
[14 empty] | 1284524 | 269637 | 31.5 | 1491970 | 393271 | 32 | 3331048 | 265487 | 31.3 | 3346578 | 285489 | 31.3 | 3479463 | 287772 | 31.7
[14 empty] | 1375231 | 313845 | 31.6 | 1650504 | 464735 | 32.3 | 3586582 | 297400 | 31.4 | 3608483 | 321498 | 31.3 | 3741461 | 328334 | 31.6
[14 empty] | 1481610 | 366292 | 31.9 | 1796366 | 545917 | 32.3 | 4067617 | 342616 | 31.4 | 4094475 | 371814 | 31.3 | 4103513 | 375924 | 31.6
[14 empty] | 1788090 | 507098 | 32.1 | 2196466 | 761829 | 32.6 | 4877656 | 446287 | 31.2 | 4906146 | 488042 | 31.2 | 5027703 | 497582 | 31.6
[14 empty] | 1951890 | 595837 | 32.2 | 2478195 | 899090 | 33.4 | 5372900 | 507981 | 31.4 | 5412419 | 558503 | 31.3 | 5641742 | 578018 | 31.6
[14 empty] | 2196042 | 705310 | 32.3 | 2713812 | 1061747 | 33.4 | 6230892 | 593957 | 31.4 | 6278110 | 654904 | 31.3 | 6348435 | 668780 | 31.6
[14 empty] | 2312828 | 760398 | 32.4 | 2854206 | 1145776 | 33.6 | 6473709 | 634119 | 31.3 | 6523616 | 699977 | 31.3 | 6576315 | 711779 | 31.6
[14 empty] | 2639603 | 895338 | 32.9 | 3261073 | 1365959 | 33.5 | 7218039 | 735068 | 31.3 | 7276074 | 814569 | 31.3 | 7331235 | 831943 | 31.5
[14 empty] | 2862458 | 1035235 | 33 | 3577960 | 1584740 | 33.7 | 8015346 | 838158 | 31.4 | 8014634 | 929953 | 31.3 | 7970933 | 944358 | 31.6
[14 empty] | 2526877 | 1033380 | 32.3 | 3154218 | 1580950 | 33.2 | 8018536 | 861261 | 30.9 | 8065404 | 953196 | 30.9 | 7825794 | 964139 | 31.2
[14 empty] | 2813141 | 1246973 | 32.5 | 3652284 | 1929315 | 33.2 | 8644680 | 994975 | 30.7 | 8757130 | 1113170 | 30.6 | 8546604 | 1125989 | 30.9
[14 empty] | 2813153 | 1247166 | 32.5 | 3652297 | 1929622 | 33.2 | 8644880 | 995093 | 30.7 | 8757212 | 1113308 | 30.6 | 8546670 | 1126123 | 30.9
[14 empty] | 3173606 | 1526998 | 32.3 | 4109203 | 2339551 | 33.5 | 9903342 | 1188588 | 30.7 | 10030390 | 1332741 | 30.6 | 9931562 | 1350490 | 30.9
[14 empty] | 3729683 | 1846369 | 32.8 | 4727135 | 2840128 | 33.6 | 11456216 | 1430560 | 30.5 | 11550441 | 1600420 | 30.5 | 11500556 | 1608396 | 30.8
[14 empty] | 4465081 | 2450050 | 33 | 6083698 | 3826891 | 34 | 14009934 | 1855445 | 30.7 | 14183992 | 2089217 | 30.6 | 14324232 | 2126042 | 30.9
[14 empty] | 5313354 | 3012430 | 33.1 | 7050987 | 4678993 | 33.9 | 16384842 | 2253039 | 30.6 | 16574599 | 2538134 | 30.5 | 16972422 | 2590764 | 30.9
[14 empty] | 6209941 | 3620102 | 33.7 | 8302894 | 5603513 | 34.4 | 18936657 | 2675943 | 30.6 | 19152812 | 3017749 | 30.5 | 19395413 | 3067130 | 31
[14 empty] | 8671372 | 5180812 | 33.5 | 11039632 | 8011001 | 34.3 | 26084969 | 3782941 | 30.5 | 26384204 | 4272888 | 30.4 | 27430047 | 4364010 | 30.6
[14 empty] | 9480138 | 6183129 | 33.9 | 12902096 | 9568163 | 34.4 | 29924022 | 4490141 | 30.5 | 30307429 | 5082385 | 30.4 | 31960318 | 5225460 | 30.7
[14 empty] | 11142439 | 7378479 | 33.8 | 14657714 | 11501066 | 34.5 | 35922625 | 5355734 | 30.2 | 36339181 | 6070380 | 30.1 | 39006071 | 6301307 | 30.4
[14 empty] | 12737827 | 8186094 | 33.4 | 16201861 | 13106135 | 34.4 | 39789172 | 5963521 | 30.3 | 40297603 | 6751955 | 30.1 | 40780175 | 6911438 | 30.6
[14 empty] | 14397040 | 9805500 | 33.7 | 19432894 | 15422997 | 34.4 | 45969026 | 7134193 | 30.5 | 46559495 | 8087500 | 30.3 | 47258074 | 8253876 | 30.8
[14 empty] | 16439536 | 11822967 | 33.9 | 22994018 | 18429259 | 34.4 | 54472134 | 8528467 | 30.4 | 55177759 | 9664973 | 30.3 | 59411998 | 10058112 | 30.6
[14 empty] | 19883393 | 14427851 | 33.5 | 27505678 | 22169127 | 34.4 | 64026329 | 10161479 | 30.4 | 64860123 | 11521669 | 30.2 | 69419776 | 11977143 | 30.5
[14 empty] | 23296493 | 17114268 | 33.8 | 31929719 | 26479739 | 34.4 | 75505338 | 12141375 | 30.4 | 76601221 | 13780168 | 30.3 | 81630764 | 14322546 | 30.5
[14 empty] | 24495645 | 17684817 | 33.7 | 33405548 | 27761126 | 34.2 | 78238586 | 12605289 | 30.3 | 79335320 | 14303855 | 30.2 | 85122186 | 14897972 | 30.5
Mid
[14 empty] | 146562 | 7314 | 16.4 | 147349 | 9086 | 16.4 | 860329 | 43001 | 23.9 | 860706 | 43149 | 23.9 | 611646 | 28193 | 17.7
[14 empty] | 149294 | 8131 | 16.4 | 151790 | 9973 | 16.5 | 842829 | 43555 | 23.9 | 843218 | 43741 | 23.9 | 598246 | 28612 | 17.6
[14 empty] | 150179 | 9303 | 16.5 | 159851 | 10963 | 16.5 | 849854 | 43871 | 23.9 | 851214 | 44118 | 23.9 | 604945 | 29203 | 17.6
[14 empty] | 163453 | 9856 | 16.5 | 164164 | 12578 | 16.5 | 886560 | 45396 | 24 | 890364 | 45822 | 24.1 | 627723 | 30654 | 17.7
[14 empty] | 163453 | 11429 | 16.5 | 170172 | 14465 | 16.6 | 916114 | 46906 | 24.1 | 918144 | 47438 | 24.1 | 648925 | 32066 | 17.7
[14 empty] | 170069 | 12900 | 16.6 | 174511 | 16822 | 16.7 | 940622 | 47961 | 24.2 | 941211 | 48523 | 24.1 | 655973 | 32948 | 17.7
[14 empty] | 173588 | 14389 | 16.7 | 181328 | 18237 | 16.7 | 960780 | 49228 | 24.2 | 962907 | 50017 | 24.2 | 771228 | 36468 | 23
[14 empty] | 175657 | 16776 | 16.7 | 184748 | 21620 | 16.8 | 1017121 | 52052 | 24.4 | 1019730 | 52961 | 24.4 | 775923 | 38091 | 22.9
[14 empty] | 188562 | 18956 | 16.8 | 201406 | 26219 | 16.9 | 1084335 | 53373 | 24.2 | 1086360 | 54703 | 24.2 | 816052 | 40545 | 23
[14 empty] | 195823 | 22759 | 16.8 | 209789 | 32316 | 17 | 1135527 | 57999 | 24.5 | 1137462 | 59565 | 24.5 | 868958 | 45856 | 23.3
[14 empty] | 201341 | 25658 | 16.9 | 224062 | 37308 | 17.1 | 1178578 | 61568 | 24.8 | 1182425 | 63539 | 24.8 | 907914 | 47791 | 23.3
[14 empty] | 222083 | 31543 | 17.1 | 251053 | 46514 | 17.3 | 1264357 | 65678 | 24.7 | 1267678 | 68130 | 24.7 | 986924 | 54884 | 23.6
[14 empty] | 239778 | 39231 | 17.1 | 269097 | 58642 | 17.4 | 1374910 | 72224 | 24.8 | 1392859 | 74609 | 24.8 | 1070625 | 61840 | 23.7
[14 empty] | 255458 | 49163 | 17.3 | 290377 | 74340 | 17.5 | 1465483 | 81171 | 25.1 | 1477114 | 85340 | 25 | 1160614 | 72606 | 24
[14 empty] | 270368 | 56395 | 17.4 | 309201 | 85910 | 17.7 | 1596916 | 87759 | 25.1 | 1606137 | 92950 | 25.1 | 1278546 | 79531 | 24
[14 empty] | 296767 | 72142 | 17.6 | 350308 | 111179 | 17.9 | 1766903 | 99937 | 25.1 | 1777366 | 106800 | 25.1 | 1401549 | 93687 | 24
[14 empty] | 302990 | 76359 | 17.7 | 355039 | 117111 | 17.9 | 1775986 | 103346 | 25.1 | 1786164 | 110501 | 25.1 | 1425656 | 98523 | 24.1
[14 empty] | 1020324 | 125737 | 30.1 | 1179551 | 175860 | 30.7 | 2798460 | 162610 | 30.8 | 2826031 | 170730 | 30.8 | 2738609 | 162611 | 30.9
[14 empty] | 1067260 | 141173 | 30.1 | 1181128 | 196549 | 30.5 | 2872194 | 167340 | 30.6 | 2891788 | 176999 | 30.6 | 2836968 | 172397 | 31
[14 empty] | 1113627 | 159664 | 30.1 | 1305815 | 228668 | 30.7 | 3008498 | 182369 | 30.5 | 3020853 | 192789 | 30.5 | 2993262 | 190592 | 30.9
[14 empty] | 1194296 | 184729 | 30.4 | 1399450 | 266207 | 31 | 3222821 | 201683 | 30.7 | 3230735 | 214276 | 30.6 | 3204535 | 211691 | 31
[14 empty] | 1288683 | 213836 | 30.6 | 1493002 | 309811 | 31.3 | 3391049 | 223526 | 30.6 | 3411340 | 238868 | 30.6 | 3417728 | 239921 | 30.9
[14 empty] | 1348380 | 233211 | 30.6 | 1579694 | 339632 | 31.3 | 3672155 | 237571 | 30.6 | 3688563 | 254313 | 30.6 | 3619239 | 257120 | 31.1
[14 empty] | 1466941 | 275623 | 31.1 | 1693947 | 399937 | 31.5 | 3933592 | 277055 | 30.7 | 3948971 | 297088 | 30.7 | 3931493 | 303899 | 31.1
[14 empty] | 1567156 | 320260 | 31.2 | 1868579 | 471896 | 31.8 | 4237729 | 309698 | 30.8 | 4255401 | 333837 | 30.8 | 4228962 | 342277 | 31.2
[14 empty] | 1682015 | 373190 | 31.4 | 2010990 | 553808 | 31.9 | 4706848 | 356303 | 30.9 | 4730679 | 385574 | 30.9 | 4623091 | 391046 | 31.2
[14 empty] | 2034859 | 515598 | 31.7 | 2474088 | 771515 | 32.2 | 5700201 | 462952 | 30.8 | 5730630 | 504783 | 30.8 | 5643974 | 516362 | 31.3
[14 empty] | 2195071 | 605085 | 31.8 | 2772450 | 909322 | 32.9 | 6242727 | 526051 | 30.9 | 6277268 | 576696 | 30.9 | 6310470 | 598954 | 31.3
[14 empty] | 2475403 | 715581 | 31.9 | 3022563 | 1073022 | 32.9 | 7155265 | 618770 | 31.1 | 7202272 | 679890 | 31.1 | 7104571 | 694319 | 31.4
[14 empty] | 2612288 | 771054 | 32 | 3168403 | 1157633 | 33.1 | 7393440 | 660585 | 31.1 | 7455017 | 726623 | 31 | 7378717 | 738256 | 31.3
[14 empty] | 2935755 | 907009 | 32.5 | 3598453 | 1379281 | 33.2 | 8242661 | 759249 | 31 | 8302770 | 839001 | 31 | 8115916 | 861439 | 31.4
[14 empty] | 3175890 | 1047970 | 32.7 | 3928470 | 1599491 | 33.4 | 9123583 | 865159 | 31.1 | 9176993 | 957169 | 31 | 8803084 | 976191 | 31.4
[14 empty] | 2800416 | 1033909 | 32.3 | 3463816 | 1581705 | 33.1 | 9002597 | 864996 | 30.8 | 9053351 | 957019 | 30.8 | 8738222 | 968169 | 31.1
[14 empty] | 3107798 | 1247589 | 32.4 | 4063436 | 1930435 | 33 | 9716923 | 999048 | 30.6 | 9840945 | 1117545 | 30.5 | 9531412 | 1130639 | 30.8
[14 empty] | 3107809 | 1247782 | 32.4 | 4063612 | 1930742 | 33 | 9717001 | 999167 | 30.6 | 9841028 | 1117684 | 30.5 | 9531479 | 1130773 | 30.8
[14 empty] | 3564305 | 1527999 | 32.2 | 4534850 | 2340847 | 33.3 | 11106521 | 1193873 | 30.6 | 11247173 | 1338423 | 30.5 | 11061704 | 1356680 | 30.9
[14 empty] | 4033068 | 1847463 | 32.8 | 5069910 | 2841685 | 33.5 | 12588985 | 1437354 | 30.5 | 12690579 | 1607482 | 30.5 | 12458949 | 1615682 | 30.8
[14 empty] | 4781428 | 2451440 | 33 | 6441046 | 3828830 | 33.9 | 15265417 | 1865237 | 30.7 | 15450775 | 2099690 | 30.6 | 15497953 | 2138267 | 30.9
[14 empty] | 5677851 | 3014277 | 33.2 | 7528215 | 4682107 | 33.8 | 17895634 | 2265936 | 30.6 | 18103968 | 2551903 | 30.5 | 18343056 | 2606954 | 30.9
[14 empty] | 6715644 | 3622720 | 33.6 | 8879910 | 5606642 | 34.2 | 20498253 | 2692346 | 30.6 | 20741257 | 3035257 | 30.5 | 21017404 | 3097600 | 30.9
[14 empty] | 9196024 | 5183916 | 33.4 | 11794994 | 8016388 | 34.1 | 28179798 | 3812443 | 30.5 | 28516222 | 4304239 | 30.5 | 28825364 | 4400025 | 30.8
[14 empty] | 10166335 | 6187310 | 33.7 | 13706907 | 9574885 | 34.2 | 32217723 | 4527564 | 30.5 | 32655726 | 5122709 | 30.5 | 33545920 | 5276428 | 30.8
[14 empty] | 11885266 | 7383573 | 33.6 | 15645119 | 11513826 | 34.2 | 38149408 | 5404573 | 30.4 | 38679017 | 6120679 | 30.3 | 40286756 | 6369559 | 30.6
[14 empty] | 13437931 | 8191907 | 33.4 | 17255994 | 13118945 | 34.2 | 42297994 | 6024623 | 30.4 | 42854019 | 6817651 | 30.3 | 42759688 | 6991350 | 30.8
[14 empty] | 15237754 | 9813644 | 33.6 | 20830352 | 15439578 | 34.1 | 49140957 | 7221853 | 30.5 | 49853529 | 8180084 | 30.4 | 50166974 | 8363008 | 30.9
[14 empty] | 18220942 | 11786793 | 33.5 | 24529564 | 18450394 | 34.1 | 57904101 | 8640909 | 30.5 | 58677342 | 9783601 | 30.4 | 60457124 | 10118417 | 30.8
[14 empty] | 21022314 | 14443723 | 33.4 | 29133864 | 22196176 | 34.2 | 68027840 | 10295408 | 30.5 | 68935550 | 11661124 | 30.4 | 71569323 | 12140414 | 30.7
[14 empty] | 24892803 | 17144204 | 33.6 | 34068253 | 26522120 | 34.1 | 80252740 | 12298818 | 30.5 | 81507529 | 13944806 | 30.4 | 84174155 | 14515719 | 30.7
[14 empty] | 26164416 | 17717685 | 33.6 | 35500824 | 27804669 | 34 | 83167964 | 12767638 | 30.4 | 84421770 | 14473107 | 30.3 | 87778169 | 15099906 | 30.7
High
[14 empty] | 197116 | 7360 | 18.8 | 198068 | 9137 | 18.8 | 1095210 | 47186 | 27 | 1095310 | 47337 | 27 | 774274 | 28693 | 19.3
[14 empty] | 200465 | 8177 | 18.9 | 203796 | 10029 | 18.9 | 1072874 | 48016 | 27.1 | 1073000 | 48202 | 27.1 | 756815 | 29180 | 19.3
[14 empty] | 201565 | 9356 | 18.9 | 214220 | 11026 | 19 | 1088648 | 48208 | 27.2 | 1089818 | 48455 | 27.2 | 769045 | 29762 | 19.3
[14 empty] | 221293 | 9918 | 19.1 | 222431 | 12644 | 19.1 | 1158974 | 49832 | 27.5 | 1163226 | 50267 | 27.5 | 807029 | 31290 | 19.5
[14 empty] | 221300 | 11492 | 19.1 | 230990 | 14540 | 19.2 | 1214285 | 51414 | 27.6 | 1216611 | 51955 | 27.6 | 856479 | 32805 | 19.6
[14 empty] | 230531 | 12969 | 19.1 | 237057 | 16901 | 19.2 | 1259378 | 52495 | 27.7 | 1259720 | 53057 | 27.7 | 865385 | 33658 | 19.6
[14 empty] | 238545 | 14464 | 19.2 | 250729 | 18325 | 19.3 | 1298307 | 53794 | 27.8 | 1300777 | 54591 | 27.8 | 1057882 | 36899 | 26.6
[14 empty] | 241821 | 16857 | 19.2 | 255950 | 21717 | 19.3 | 1409288 | 56746 | 27.9 | 1411857 | 57654 | 28 | 1072454 | 38519 | 26.4
[14 empty] | 264896 | 19048 | 19.4 | 281731 | 26327 | 19.5 | 1493310 | 58044 | 27.7 | 1495689 | 59385 | 27.7 | 1129544 | 41006 | 26.5
[14 empty] | 274090 | 22862 | 19.4 | 294233 | 32444 | 19.6 | 1601730 | 62781 | 28.1 | 1603649 | 64347 | 28.1 | 1233807 | 46848 | 27
[14 empty] | 281724 | 25765 | 19.5 | 324861 | 37455 | 20 | 1699595 | 66793 | 28.4 | 1704030 | 68774 | 28.5 | 1305800 | 48728 | 26.8
[14 empty] | 322203 | 31671 | 19.6 | 374739 | 46682 | 20.1 | 1835964 | 70815 | 28.3 | 1839520 | 73266 | 28.3 | 1452122 | 56077 | 27.4
[14 empty] | 357730 | 39378 | 20 | 401623 | 58834 | 20.2 | 2039097 | 77519 | 28.4 | 2053069 | 79803 | 28.2 | 1603076 | 63092 | 27.5
[14 empty] | 381657 | 49338 | 20.2 | 433262 | 74564 | 20.4 | 2217717 | 86530 | 28.6 | 2226071 | 90889 | 28.7 | 1758415 | 74102 | 27.8
[14 empty] | 421505 | 56580 | 20.2 | 478105 | 86158 | 20.5 | 2426059 | 93628 | 28.7 | 2437092 | 98842 | 28.7 | 1968389 | 81157 | 27.6
[14 empty] | 458518 | 72364 | 20.4 | 547437 | 111499 | 20.7 | 2745920 | 106097 | 28.6 | 2759030 | 112987 | 28.6 | 2205953 | 98845 | 28.1
[14 empty] | 471119 | 76603 | 20.5 | 552695 | 117433 | 20.7 | 2783070 | 109612 | 28.6 | 2795589 | 116781 | 28.7 | 2241666 | 100431 | 27.7
[14 empty] | 1514327 | 126079 | 33.1 | 1764062 | 176321 | 33.7 | 3966031 | 163953 | 33.3 | 4015566 | 172109 | 33.4 | 3827727 | 164379 | 33.4
[14 empty] | 1588955 | 141519 | 33.1 | 1770171 | 196966 | 33.6 | 3957144 | 168601 | 33 | 3983516 | 178304 | 33 | 3948874 | 173757 | 33.4
[14 empty] | 1710001 | 160015 | 33 | 1996806 | 229151 | 33.6 | 4227787 | 183704 | 33 | 4243623 | 194135 | 33 | 4266627 | 192030 | 33.4
[14 empty] | 1826278 | 185140 | 33.3 | 2129784 | 266755 | 33.8 | 4554880 | 203210 | 33.1 | 4567139 | 215823 | 33.1 | 4582082 | 213338 | 33.5
[14 empty] | 1966567 | 214302 | 33.5 | 2262336 | 310422 | 34 | 4824832 | 225144 | 33.2 | 4851327 | 240513 | 33.2 | 4889067 | 241774 | 33.4
[14 empty] | 2053523 | 233689 | 33.5 | 2379584 | 340260 | 34 | 5224297 | 239326 | 33.1 | 5246255 | 256084 | 33.1 | 5214331 | 259162 | 33.5
[14 empty] | 2218921 | 276206 | 33.8 | 2564864 | 400653 | 34.2 | 5570139 | 279039 | 33.1 | 5591364 | 299089 | 33.1 | 5581276 | 306316 | 33.4
[14 empty] | 2370064 | 320903 | 34 | 2824978 | 472736 | 34.4 | 6032833 | 311955 | 33.2 | 6057645 | 336124 | 33.2 | 6026318 | 345057 | 33.5
[14 empty] | 2525026 | 373893 | 34.1 | 3018134 | 554728 | 34.5 | 6797031 | 359153 | 33.3 | 6830473 | 388472 | 33.3 | 6619086 | 394350 | 33.5
[14 empty] | 3113390 | 516505 | 34.1 | 3759714 | 772714 | 34.6 | 8343067 | 466558 | 33.2 | 8386631 | 508438 | 33.3 | 8268670 | 520784 | 33.5
[14 empty] | 3342122 | 606090 | 34.3 | 4176905 | 916954 | 34.7 | 9151441 | 530174 | 33.2 | 9210955 | 580902 | 33.3 | 9201564 | 608667 | 33.5
[14 empty] | 3686979 | 716746 | 34.5 | 4518011 | 1082312 | 34.9 | 10593424 | 624413 | 33.4 | 10629633 | 688145 | 33.4 | 10591605 | 699847 | 33.7
[14 empty] | 3904247 | 772336 | 34.5 | 4728457 | 1167413 | 35 | 10940993 | 665999 | 33.4 | 11039196 | 732174 | 33.5 | 10982053 | 744326 | 33.6
[14 empty] | 4364125 | 914643 | 34.4 | 5263165 | 1389746 | 34.9 | 12274269 | 765555 | 33.5 | 12365824 | 845504 | 33.5 | 12151782 | 868610 | 33.7
[14 empty] | 4775385 | 1058497 | 34.6 | 5747796 | 1610398 | 35.1 | 13698433 | 872624 | 33.5 | 13785707 | 964808 | 33.5 | 13156287 | 984382 | 33.7
[14 empty] | 4222493 | 1044049 | 34.1 | 5088034 | 1592040 | 34.6 | 13371066 | 872465 | 33.2 | 13454242 | 964664 | 33.2 | 12894915 | 976231 | 33.4
[14 empty] | 4627434 | 1258183 | 34.2 | 6002358 | 1938682 | 34.4 | 14495285 | 1007195 | 33 | 14665495 | 1126296 | 33.1 | 14123130 | 1139940 | 33.3
[14 empty] | 4627447 | 1258376 | 34.2 | 6002372 | 1938989 | 34.4 | 14495381 | 1007314 | 33 | 14665600 | 1126435 | 33.1 | 14123218 | 1140074 | 33.3
[14 empty] | 5230391 | 1530002 | 34.1 | 6709917 | 2351515 | 34.6 | 16767711 | 1211009 | 33 | 16962627 | 1356208 | 33 | 16752508 | 1375652 | 33.1
[14 empty] | 6149024 | 1856236 | 34 | 7675666 | 2853698 | 34.6 | 19358699 | 1450942 | 33 | 19523830 | 1621607 | 33.1 | 18907698 | 1630253 | 33.1
[14 empty] | 7227401 | 2462647 | 34.2 | 9870606 | 3839798 | 35 | 23638581 | 1884821 | 33.1 | 23636343 | 2120637 | 33.1 | 23650700 | 2162716 | 33.2
[14 empty] | 8571231 | 3029751 | 34.4 | 11397312 | 4699614 | 34.8 | 27512315 | 2291729 | 33 | 27816179 | 2579441 | 33 | 27973675 | 2639336 | 33.1
[14 empty] | 10268934 | 3637735 | 34.6 | 13694323 | 5624905 | 35.2 | 31851278 | 2725152 | 33.1 | 32212194 | 3070272 | 33.1 | 31987730 | 3134775 | 33.2
[14 empty] | 13831944 | 5200564 | 34.8 | 18296349 | 8028338 | 34.9 | 44071995 | 3873036 | 33 | 44631353 | 4366942 | 33.1 | 44795476 | 4472056 | 33
[14 empty] | 15736981 | 6203560 | 34.8 | 20806682 | 9599728 | 35.1 | 50805066 | 4602410 | 33 | 51442665 | 5203358 | 33.1 | 52282050 | 5383371 | 33
[14 empty] | 18117843 | 7403001 | 34.6 | 23940619 | 11539347 | 34.9 | 60242255 | 5502250 | 32.9 | 60925529 | 6231363 | 32.9 | 63696692 | 6506064 | 32.6
[14 empty] | 20141170 | 8214826 | 34.7 | 27094020 | 13144564 | 35.1 | 66937221 | 6146828 | 32.9 | 67784356 | 6949042 | 32.9 | 67015810 | 7151175 | 33
[14 empty] | 23597897 | 9839475 | 34.6 | 32214912 | 15472740 | 35 | 77652391 | 7390715 | 32.9 | 78641577 | 8362809 | 33 | 78185949 | 8632837 | 33
[14 empty] | 26891047 | 11821470 | 34.7 | 37887803 | 18492664 | 35 | 91436631 | 8865792 | 32.9 | 92569202 | 10020858 | 33 | 95960942 | 10480505 | 32.7
[14 empty] | 33107489 | 14475465 | 34.5 | 43628166 | 22366806 | 35.1 | 108658487 | 10563268 | 33 | 110037279 | 11940033 | 33 | 113622760 | 12466957 | 32.7
[14 empty] | 37999638 | 17204075 | 34.5 | 53772983 | 27182263 | 34.9 | 128437987 | 12613703 | 33 | 130256573 | 14274082 | 33 | 133631927 | 14902067 | 32.7
[14 empty] | 39899905 | 17783421 | 34.5 | 54980699 | 28044043 | 34.8 | 133199429 | 13092335 | 33 | 135028205 | 14811611 | 33 | 139168531 | 15503774 | 32.7