## Project Description
Akron Rack 40 On-Demand PAA Pilot description
The project entailed deployment of an on-site on-demand peracetic acid (PAA) disinfectant pilot system at a combined sewer storage facility in Akron, OH (Akron Rack 40). The pilot system was constructed and wet tested in Cincinnati, OH at EPA facilities and transported via trailer to the Akron site. The system produced a dilute peracetic acid disinfection solution via reaction of two industrial detergent powders (TAED - Tetraacetylethylenediamine and SPC - Sodium percarbonate) in a water matrix. The disinfectant was injected into a simulated combined sewer overflow (CSO) stream via mixing Little Cuyahoga River water with raw sewage drawn from the Akron sewer system. Samples were drawn after 5-minute, 10-minute and 15-minute contact time to determine efficacy of the system at reducing pathogens as primarily determined through E. coli inactivation. Sample sets from two trials were also analyzed for inactivation of Heterotrophic bacteria and Bacteriophage MS2 as surrogate for viral inactivation. |  |  | These analytical results were collected in accordance with an approved Quality Assurance Project Plan. These results have been reviewed by internal US EPA technical experts, quality assurance staff, and management. Any mention of trade names or commercial products does not constitute US EPA endorsement or recommendation for use.
MOBILE PAA GENERATOR LAYOUT DIAGRAM
Tab Descriptors
|  | EPA Samples | Samples from 11 trial runs conducted by EPA Team
|  | Field Measurements | Data obtained in field during EPA Team trials
|  | Akron WRF Samples | Samples from trial runs conducted by Akron WRF staff in paralell to EPA trials
|  | MS2 | Samples from two EPA trial runs analyzed by EPA lab in Cincinnati
Data Dictionary
|  | MPN/dl | Most Probable Number/deciliter (100 ml)
|  | mg/l | milligram/liter
|  | ppm | parts per million
|  | PFU/ml | Plaque-forming Unit/milliliter
|  | CFU/ml | Colony-forming Unit/milliliter
|  | gm/l | grams/liter
|  | gpm | gallons per minute
|  | PAA | Peracetic Acid
|  | TAED | Tetraacetylethylenediamine
|  | SPC | Sodium percarbonate
|  | CSO | Combined Sewer Overflow
|  | EDTA | Ethylenediaminetetraacetic acid
|  | E. coli | Escherichia coli
|  | TSS | Total Suspended Solids
|  | COD | Chemical Oxygen Demand
|  | MS2 | Bacteriophage MS2 (Emesvirus zinderi)
|  | HPC | Heterotrophic plate count

## EPA Samples
Sample ID nomenclature | 1st digit | T# |  |  | Last digits
| Trial # | Contact time designation |  | T0 - influent prior to disinfection | Target dose (ppm)
T1- 5 minute contact time
T2- 10 minute contact time
T3- 15 minute contact time
Example 2-T3-20 | Trial 2 15 minute contact time at 20 ppm target dose
Sample ID | Sample Date | E. Coli (MPN/dL) | TSS (mg/L) | COD (mg/L)
1-T0-20 | 2024-07-24 | 1920000 | 61 | 165
1-T1-20 | 2024-07-24 | 2020 | n/d | n/d |  | Measurement | Sample Container | Volume of Sample | Preservation | Holding Time | Laboratory | Analytical Method
1-T2-20 | 2024-07-24 | 2950 | n/d | n/d |  | E. Coli | Plastic or Glass | 100 mL | Sodium Thiosulfate, 4˚C +/- 2 | 8 Hours | Akron WRF Lab | SM 9223 B
1-T3-20 | 2024-07-24 | 484 | n/d | n/d |  | Total Suspended Solids | Plastic or Glass | 1000 mL | 4˚C +/- 2 | 7 Days | Akron WRF Lab | SM 2540 D
[6 empty] | Chemical Oxygen Demand | Plastic or Glass | 100 mL | 4˚C +/- 2, H2SO4 to pH <2 | 28 Days | Akron WRF Lab | SM 5220 D
2-T0-20 | 2024-07-24 | 2480000 | 50 | 164
2-T1-20 | 2024-07-24 | 2650 | n/d | n/d
2-T2-20 | 2024-07-24 | 320 | n/d | n/d
2-T3-20 | 2024-07-24 | 20 | n/d | n/d
2-T3-20D | 2024-07-24 | 40 | n/d | n/d
3-T0-30 | 2024-07-24 | 2770000 | 56 | 161
3-T1-30 | 2024-07-24 | 724 | n/d | n/d
3-T2-30 | 2024-07-24 | <20 | n/d | n/d
3-T3-30 | 2024-07-24 | <20 | n/d | n/d
4-T0-20 | 2024-07-24 | 2260000 | 44 | 129
4-T1-20 | 2024-07-24 | 1770 | n/d | n/d
4-T1-20D | 2024-07-24 | 1490 | n/d | n/d
4-T2-20 | 2024-07-24 | <20 | n/d | n/d
4-T2-20 NON-DILUTE | 2024-07-24 | 61.7 | n/d | n/d
4-T3-20 | 2024-07-24 | 54.8 | n/d | n/d
5-T0-15 | 2024-07-24 | 2480000 | 44 | 148
5-T1-15 | 2024-07-24 | 2760 | n/d | n/d
5-T2-15 | 2024-07-24 | 2320 | n/d | n/d
5-T3-15 | 2024-07-24 | 422 | n/d | n/d
5-T3-15 NON-DILUTE | 2024-07-24 | >2419.6
6-T0-15 | 2024-07-25 | 2770000 | 34 | 110
6-T1-15 | 2024-07-25 | 3360 | n/d | n/d
6-T2-15 | 2024-07-25 | 2100 | n/d | n/d
6-T3-15 | 2024-07-25 | 2440 | n/d | n/d
7-T0-10 | 2024-07-25 | 1670000 | 36 | 123
7-T1-10 | 2024-07-25 | 96800 | n/d | n/d
7-T2-10 | 2024-07-25 | 2560 | n/d | n/d
7-T2-10D | 2024-07-25 | 2780 | n/d | n/d
7-T3-10 | 2024-07-25 | 2170 | n/d | n/d
8-T0-5 | 2024-07-31 | 1670000 | 78 | 152
8-T1-5 | 2024-07-31 | >96800 | n/d | n/d
8-T2-5 | 2024-07-31 | >96800 | n/d | n/d
8-T3-5 | 2024-07-31 | >96800 | n/d | n/d
9-T0-20 | 2024-07-31 | 1790000 | 56 | 174
9-T1-20 | 2024-07-31 | 4450 | n/d | n/d
9-T2-20 | 2024-07-31 | 5400 | n/d | n/d
9-T3-20 | 2024-07-31 | 7310 | n/d | n/d
10-T0-15 | 2024-07-31 | 3180000 | 44 | 155
10-T1-15 | 2024-07-31 | 440 | n/d | n/d
10-T2-15 | 2024-07-31 | 976 | n/d | n/d
10-T2-15 DUPLICATE | 2024-07-31 | 662 | n/d | n/d
10-T3-15 | 2024-07-31 | 238 | n/d | n/d
11-T0-10 | 2024-07-31 | 2770000 | 57 | 160
11-T1-10 | 2024-07-31 | >96800 | n/d | n/d
11-T2-10 | 2024-07-31 | 79400 | n/d | n/d
11-T3-10 | 2024-07-31 | 14600 | n/d | n/d

## Field Measurements
Trial | PAA Feedwater | PAA Stock Solution Concentration (%) | Target Dose (ppm) | Immediate Residual (ppm) | Final Residual (ppm)
1 | Potable | 1.3 | 20 | n/d | n/d | All trials conducted at 10 gpm forward flowrate
2 | Potable | 1.3 | 20 | 1.72 | n/d | Test water - Simulated CSO at ~ 33% raw sewage/67% Little Cuyahoga River Water
3 | Potable | 1.3 | 30 | 24 | 16.25
4 | Potable | 1.45 | 20 | 23 | 11.35 | Stock Solution
5 | Potable | 1.45 | 15 | 24 | 7.4 | 70 gm/l TAED - 70 gm/l SPC
6 | Little Cuyahoga | 2.3 | 15 | 11.25 | 4.4
7 | Little Cuyahoga | 2.3 | 10 | 17.2 | 3.02 | Measurement | Sample Container | Volume of sample | Preservation | Holding Time | Laboratory | Analytical Method
8 | Simulated CSO** | 2.58 | 5 | 1.02 | 0.88 | Total Residual PAA | Glass beaker | 100 mL | None | Measurements to be taken at the time of sampling | Field | 4500-PAA-2019 (DPD)
9 | Simulated CSO | 2.58 | 20 | 2.64 | 4.55
10 | Simulated CSO | 2.58 | 15 | 21.5 | 8.7
11 | Simulated CSO | 1.36 | 10 | 5.2 | 0.8
** 2.5 gallon test batch of PAA stock solution using Simulated CSO feedwater
| Reaction Time (min.) | PAA Stock Solution Concentration (%)
| 10 | 0.52
| 20 | 1.47
| 30 | 1.21
| 35 | 1.43

## Akron WRF Samples
Sample ID | Sample Date | E. Coli (MPN/dL) | TSS (mg/L) | COD (mg/L)
T1-H10 | 2024-07-24 | 28300 | n/d | n/d
T1-P10 | 2024-07-24 | 100 | n/d | n/d
[5 empty] | Measurement | Sample Container | Volume of Sample | Preservation | Holding Time | Laboratory | Analytical Method
T2-H20 | 2024-07-24 | 4670 | n/d | n/d | E. Coli | Plastic or Glass | 100 mL | Sodium Thiosulfate, 4˚C +/- 2 | 8 Hours | Akron WRF Lab | SM 9223 B
T2-P20 | 2024-07-24 | 82 | n/d | n/d | Total Suspended Solids | Plastic or Glass | 1000 mL | 4˚C +/- 2 | 7 Days | Akron WRF Lab | SM 2540 D
[5 empty] | Chemical Oxygen Demand | Plastic or Glass | 100 mL | 4˚C +/- 2, H2SO4 to pH <2 | 28 Days | Akron WRF Lab | SM 5220 D
T3-P30 | 2024-07-24 | 20 | n/d | n/d
T3-H30 | 2024-07-24 | 6150 | n/d | n/d | T | Trial #
[5 empty] | H designation | hypochlorite disinfectant
AK Effluent | 2024-07-25 |  | 39 | n/d | P designation | peracetic acid disinfectant
AK River | 2024-07-25 |  | 3.2 | n/d | Digits | Target dose (ppm)
AK RAW | 2024-07-25 | >3870000 | 58 | n/d | AK | Akron
T1H10 | 2024-07-25 | >48400 | n/d | n/d
T2H15 | 2024-07-25 | >48400 | n/d | n/d
T1P10 | 2024-07-25 | 39700 | n/d | n/d
T1P10 | 2024-07-31 | 18400 | n/d | n/d
T1H10 | 2024-07-31 | 18400 | n/d | n/d
T2P15 | 2024-07-31 | >96800 | n/d | n/d
T2H15 | 2024-07-31 | >96800 | n/d | n/d
T3P10 | 2024-07-31 | 19500 | n/d | n/d
T3H10 | 2024-07-31 | 30800 | n/d | n/d
T4P15 |  | 9960 | n/d | n/d
T4H15 | 2024-07-31 | >96800 | n/d | n/d
AK Effluent 815 | 2024-07-31 |  | 43 | n/d
AK Effluent 1230 | 2024-07-31 |  | 57 | n/d

## MS2
Sample | Date | MS2 (PFU/mL) | Total Coliform (CFU/mL) | E.coli (CFU/mL) | HPC (CFU/mL)
10-T0-15 | 2024-07-31 | 6100 | 135000 | 30000 | 1255000
10-T1-15 | 2024-07-31 | 4010 | 10 | 5 | 8850
10-T2-15 | 2024-07-31 | 3550 | 20 | 5 | 7850
10-T3-15 | 2024-07-31 | 4425 | 5 | 5 | 10800
11-T0-10 | 2024-07-31 | 5550 | 155000 | 20000 | 1195000
11-T1-10 | 2024-07-31 | 5765
11-T1-10 DUPLICATE | 2024-07-31 | 4960
11-T2-10 | 2024-07-31 | 4830 | 10650 | 345 | 126500
11-T3-10 | 2024-07-31 | 3700 | 1250 | 20 | 1035000
|  | U.S. Environmental Protection Agency (USEPA). Method 1601: Male-specific (F+) and somatic coliphage in water by two-step enrichment procedure, 2001, Washington, DC. | US Environmental Protection Agency Method 1604 (2002) Total Coliforms and Escherichia coli in Water by Membrane Filtration Using a Simultaneous Detection Technique (MI Medium). Rept. Mo. EPA 821-R-02-024, Environmental Protection Agency, Washington DC. |  | Standard Methods Committee of the American Public Health Association, American Water Works Association, and Water Environment Federation. 9215 heterotrophic plate count In: Standard Methods For the Examination of Water and Wastewater. Lipps WC, Baxter TE, Braun-Howland E, editors. Washington DC: APHA Press.