## Read-Me
Description |  | The worksheet contains microbial, disinfection byproduct (DBP), and other water quality parameters at public water systems distribution network.
Technology |  | Purge and trap (P&T) with gas chromatography-mass spectrometry (GC-MS)
Gas chromatography-mass spectrometry (GC-MS)
Atomic Emission Spectroscopy (AES)
Ion Chromotography (IC)
Total organic carbon (TOC) analyzer
Thermometer
quantitative PCR
Spectrometer
pH meter
Units |  | DBP data: micrograms (ug)/ liter (L)
Water quality parameters milligrams: (mg)/L
Metals/Anions/Total Organic Carbon (TOC): mg/L
Molecular data: genomic unit (GU)/L
Culture data: colony forming unit (CFU) or most probable number (MPN)/L
Water type |  | distribution water
Column A | Water Collection Date | date
Column B | Utility designation | PT, GG, CA, JB, RM, and SW (These two letter designations have no meaning and were only used to identify the utility)
Column C | Location | Entry Point (EP), Mid Point (MP), Maximum Residence Time (MRT), Tank, Total Coliform Rule (TCR) location, Disinfection Byproduct (DBP) and Source Water (SW) location
Column D | Source Water type | Surface water (SW) or groundwater (GW)
Column E | Disinfectant | Cl for Chlorine and CLM for chloramine
Column F | Distance from EP | number of miles away sampling location is from entry point sampling location
Column G-S | Water quality parameter | pH, temperature, nitrite, total chlorine, monochloramine, free chlorine, free ammonia, water hardness, disolved oxygen
Column T-AP | Microbe data | Heterotrophic bacteria (HPC), Nontuberculous Mycobacteria (NTM), Pseudomonas spp., Coliform, E. coli, Amoeba, Mycobacteria avium, M. intracellulare, M. abscessus, Legionella spp. (Genus), Legionella pneumophila, Legionella maceachernii (Mace), Legionella micdadei (Mic), Legionella anisa, Legionellabozemanii, Legionella longbeachae, and Pseudomonas aeruginosa
Column AR-BY | Metals/Anions/TOC | Arsenic (As), Barium (Ba), Beryllium (Be) Bromide (Br), Calcium (Ca), Cadmium (Cd), Chloride (Cl), Chromium (Cr), Copper (Cu) Iron (Fe), Fluoride (F), Potassium (K), Lithium (Li), Magnesium (Mg) manganese (Mn), Sodium (Na), Nickle (Ni), Nitrite (NO2), Nitrate (NO3), Lead (Pb), Phosphate (PO4), Phosphrous (P), Anitmony (Sb), Silica (Si), tin (Sn), Sulfate (SO4), Strontium (Sr), Sulfur (S), Total Organic Carbon (TOC), Vanadium (V), and Zinc (Zn)
| Note: | Limit of detection is reported as a negative number. This is how this lab reported their data.
Column CA-DE | DBPs | chloroform, bromodichloromethane, dibromochloromethane, bromoform, dichloroiodomethane, bromochloroiodomethane, dibromoiodomethane, chlorodiiodomethane , bromodiiodomethane, iodoform, trichloronitromethane, dichloronitromethane, bromonitromethane, bromochloronitromethane, tribromonitromethane, trichloroacetic acid, dichloroacetic acid, monochloroacetic acid, dibromoacetic acid, monobromoacetic acid, bromochloroacetic acid, bromodichloroacetic acid, chlorodibromoacetic acid, tribromoacetic acid, trichloroacetonitrile, dichloroacetonitrile, bromoacetonitrile, bromochloroacetonitrile, dibromoacetonitrile, 1,1-dichloropropane, and 1,1,1-trichloropropanone
Abbreviation |  | Cq= Cycle of quantification
Last Update |  | 2026-06-26

## Scihub
[6 empty] | Water Quality Parameters | [12 empty] | Micobiology Test | [22 empty] | Metals/Anion/Total Organic Carbon | [33 empty] | Disinfection Byproducts
Water Collection Date | Utility Designation | Location | Source Water | Disinfectant | Distance from EP | pH | temperature | temperature | Nitrite | Utility Total Chlorine | Utility Free Chlorine | Researcher monochloramine | Researcher Total Chlorine | Researcher Free Chlorine | Researcher monochloramine | Free Ammonia | Hardness | Disolved Oxygen | HPC | Colilert | Colilert-E.coli | Pseudomonas sp. | NTM | Amoeba Final | BCYE | BCYE | BCYE | BCYE | M. avium | M. intracellulare | M. abscessus | Pseudomonas aeruginosa | Legionella spp. PAN | Legionella spp. confirmation assay-16S |  | L. pneumophila | L. maceachernii (Mace) | L. micdadei (Mic) | L. anisa | L. bozemanii | L. longbeachae | AL_AES | AS_AES | BA_AES | BE_AES | BR | CA_AES | CD_AES | CL_IC | CR_AES | CU_AES | FE_AES | F_IC | K_AES | LI_AES | MG_AES | MN_AES | NA_AES | NI_AES | NO2_IC | NO3ICasN | NO3N | PB_AES | PO4ICasP | P_AES | SB_AES | SI_AES | SN_AES | SO4_IC | SR_AES | S_AES | TN | TOC_COMB | V_AES | ZN_AES | Chloroform | Trichloroacetonitrile | Bromodichloromethane | 1,1-Dichloro-2-propanone | Dichloroacetonitrile | Chloropicrin (Trichloronitromethane) | Dichloronitromethane | Dibromochloromethane | Bromoacetonitrile | Dichloroiodomethane | 1,1,1-Trichloro-2-propanone | Bromonitromethane | Bromochloroacetonitirle | Bromochloronitromethane | Bromoform | Bromochloroiodomethane | Dibromoacetonitrile | Dibromoiodomethane | Chlorodiiodomethane | Bromopicrin (Tribromonitromethane) | Bromodiiodomethane | Iodoform | Trichloroacetic acid | Dichloroacetic acid | Monochloroacetic acid | Dibromoacetic acid | Monobromoacetic acid | Bromochloroacetic acid | Bromodichloroacetic acid | Chlorodibromoacetic acid | Tribromoacetic acid
Limit of Detection (LOD) | [8 empty] | 0.005 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 |  |  | 5000 | 5 | 5 | 1000 | 1 | presence/absence | 5000 | Notes | L spp Positive | Lp positive | 84 | 80 | 20 | 14 | 40 | Rx1 | Rx2 | 80 | 44 | 8 | 32 | 44 | 16 | 0.004 | 0.004 | 0.001 | 0.005 | -0.008 | 0.01 | -0.0003 | -0.03 | -0.001 | -0.001 | -0.001 | -0.007 | -0.3 | -0.005 | -0.005 | -0.001 | -0.03 | -0.001 | -0.005 | -0.006 | -0.02 | -0.002 | -0.011 | -0.005 | -0.003 | -0.02 | -0.001 | -0.05 | -0.001 | -0.003 | -0.01 | -0.23 | -0.001 | -0.0005 | 0.05 | 0.1 | 0.05 | 0.5 | 0.1 | 1 | 0.1 | 0.05 | 0.1 | 0.05 | 0.5 | 1 | 0.5 | 1 | 0.05 | 0.05 | 1 | 0.05 | 0.05 | 1 | 0.05 | 0.1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 4
Units | [6 empty] | F | C | mg N/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L NO2-N | mg/L | mg/L | CFU/L | MPN/1L | MPN/1L | CFU/L | CFU/L |  | CFU/L |  |  |  | GU/L | GU/L | GU/L | GU/L | GU/L | Cq/100mL | Cq/100mL | GU/L | GU/L | GU/L | GU/L | GU/L | GU/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L
2025-02-05 | CV | EP | SW | CL | not given | 7.63 | 47.66 | 8.7 | 0.006 | 1.58 | 1.36 | not measured | 1.49 | 1.39 | not measured | not measured | 51.36 | 9.8 | 7500 | 5 | 5 | 1000 | Bacillus | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0078 | -0.004 | 0.0177 | -0.005 | -0.008 | 13.71 | -0.0003 | 10.0728 | -0.001 | 0.0029 | 0.0024 | 0.7852 | 1.436 | -0.005 | 1.351 | -0.001 | 7.873 | -0.001 | -0.005 | 0.3673 | Not meassured | -0.002 | 0.8383 | 0.6821 | -0.003 | 4.249 | -0.001 | 24.4708 | 0.0318 | 8.101 | 0.24 | 0.683 | -0.001 | 0.0044 | 22.8626 | 0.05 | 4.6276 | 0.25 | 0.36933 | 0.5 | 0.05 | 0.86635 | 0.05 | 0.10642 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-05 | CV | MP | SW | CL | not given | 7.88 | 52.52 | 11.4 | not measured | 1.42 | 1.33 | not measured | 1.39 | 1.32 | not measured | not measured | 51.36 | 10.1 | 5000 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0096 | -0.004 | 0.0162 | -0.005 | -0.008 | 14.92 | -0.0003 | 10.9662 | -0.001 | 0.0023 | 0.0198 | 0.702 | 1.533 | -0.005 | 1.475 | 0.0057 | 8.714 | -0.001 | -0.005 | 0.3881 | Not meassured | -0.002 | 0.7084 | 0.685 | -0.003 | 4.425 | -0.001 | 22.3793 | 0.0359 | 7.493 | 0.235 | 0.511 | -0.001 | 0.0061 | 31.6155 | 0.05 | 5.6618 | 0.25 | 0.35313 | 0.5 | 0.13836 | 1.2277 | 0.05 | 0.12995 | 0.25 | 0.5 | 0.25 | 0.5 | 0.06579 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-05 | CV | MRT | SW | CL | not given | 7.64 | 44.96 | 7.2 | 0.006 | 1.49 | 1.24 | not measured | 1.68 | 1.55 | not measured | not measured | 68.48 | 10.01 | 5000 | 5 | 5 | 1000 | Bacillus | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0102 | -0.004 | 0.0191 | -0.005 | -0.008 | 14.53 | -0.0003 | 11.1965 | -0.001 | 0.001 | 0.02 | 0.7176 | 1.542 | -0.005 | 1.485 | 0.0017 | 8.958 | -0.001 | -0.005 | 0.3766 | Not meassured | -0.002 | 0.7357 | 0.7099 | -0.003 | 4.374 | -0.001 | 22.7004 | 0.0365 | 7.639 | 0.24 | 0.468 | -0.001 | 0.003 | 29.0451 | 0.05 | 4.9107 | 0.25 | 0.29357 | 0.5 | 0.15013 | 0.93379 | 0.05 | 0.11194 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-05 | CV | TANK | SW | CL | not given | 7.81 | 57.56 | 14.2 | 0.006 | 1.14 | 1.06 | not measured | 1.11 | 1.03 | not measured | not measured | 51.36 | 10.22 | 5000 | 5 | 5 | 1000 | Bacillus | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.017 | -0.004 | 0.0192 | -0.005 | -0.008 | 14.14 | -0.0003 | 9.7905 | -0.001 | 0.0049 | 0.065 | 0.731 | 1.504 | -0.005 | 1.474 | 0.0013 | 8.169 | -0.001 | -0.005 | 0.3054 | Not meassured | -0.002 | 0.7353 | 0.6762 | -0.003 | 4.587 | -0.001 | 22.2718 | 0.035 | 7.59 | 0.256 | 0.589 | -0.001 | 0.0102 | 35.5916 | 0.05 | 6.457 | 0.25 | 0.40782 | 0.5 | 0.17628 | 1.5291 | 0.05 | 0.14304 | 0.25 | 0.5 | 0.25 | 0.5 | 0.10552 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-05 | CV | TCR | SW | CL | not given | 7.68 | 52.52 | 11.4 | not measured | 1.38 | 1.24 | not measured | 1.33 | 1.22 | not measured | not measured | 51.36 | 9.73 | 35000 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0097 | -0.004 | 0.0169 | -0.005 | -0.008 | 14.2 | -0.0003 | 10.0076 | -0.001 | 0.0082 | 0.0063 | 0.7093 | 1.574 | -0.005 | 1.402 | -0.001 | 8.19 | 0.0041 | -0.005 | 0.3051 | Not meassured | -0.002 | 0.6683 | 0.664 | -0.003 | 4.299 | -0.001 | 22.7919 | 0.0342 | 7.769 | 0.244 | 0.51 | -0.001 | 0.007 | 37.9936 | 0.05 | 6.5254 | 0.25 | 0.37033 | 0.5 | 0.22946 | 1.5157 | 0.05 | 0.14702 | 0.25 | 0.5 | 0.25 | 0.5 | 0.095874 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-05 | CV | DBP | SW | CL | not given | 7.58 | 48.2 | 9 | not measured | 1.38 | 1.2 | not measured | 1.35 | 1.3 | not measured | not measured | 51.36 | 9.6 | 12500 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0085 | -0.004 | 0.0163 | -0.005 | -0.008 | 13.84 | -0.0003 | 9.7884 | -0.001 | 0.0013 | 0.0153 | 0.6991 | 1.523 | -0.005 | 1.412 | 0.0015 | 8.175 | -0.001 | -0.005 | 0.3077 | Not meassured | -0.002 | 0.7158 | 0.6767 | -0.003 | 4.355 | -0.001 | 22.0364 | 0.0338 | 7.5 | 0.259 | 0.515 | -0.001 | 0.0037 | 28.3623 | 0.05 | 5.2874 | 0.25 | 0.35045 | 0.5 | 0.1616 | 1.1631 | 0.05 | 0.11819 | 0.25 | 0.5 | 0.25 | 0.5 | 0.055979 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-05 | CV | SW | SW | CL | not given | 7.75 | 40.28 | 4.6 | 0.004 | 0 | 0 | not measured | 0.02 | 0 | not measured | not measured | 34.24 | 9.52 | 10000000 | 2660 | 50 | 10000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 2141888.3295 | 2039 | 1416 | 277369.2756 | 28.2125 | 29.969 | 4246 | 436 | 1830.7968 | 32 | 44 | 16 | 0.1071 | -0.004 | 0.0183 | -0.005 | -0.008 | 4.621 | -0.0003 | 6.9463 | -0.001 | 0.003 | 0.399 | 0.0639 | 1.443 | -0.005 | 1.346 | 0.0291 | 4.912 | -0.001 | 0.1106 | 0.3639 | Not meassured | -0.002 | -0.011 | 0.0314 | -0.003 | 4.817 | -0.001 | 2.6252 | 0.0235 | 0.921 | 0.441 | 1.624 | -0.001 | 0.0034 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-23 | CV | EP | SW | CL | not given | 7.54 | 66.92 | 19.4 | 0.006 | 1.86 | 1.58 | not measured | 1.45 | 1.33 | not measured | not measured | 51.36 | 6.17 | 17500 | 0 | 0 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 11.5584 | Not meassured | Not meassured | Not meassured | 0.6253 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0185 | 0.0451 | Not meassured | Not meassured | 0.4866 | Not meassured | Not meassured | Not meassured | Not meassured | 18.0512 | Not meassured | Not meassured | 0.076 | 0.815 | Not meassured | Not meassured | 64.2505 | 0.05 | 15.0374 | 0.25 | 0.58926 | 0.5 | 0.74118 | 2.7395 | 0.05 | 0.37353 | 0.25 | 0.5 | 0.25 | 0.5 | 0.16959 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-23 | CV | MP | SW | CL | not given | 8.18 | 64.4 | 18 | not measured | 1.22 | 1.1 | not measured | 1.01 | 0.82 | not measured | not measured | 51.36 | 6.04 | 25000 | 5 | 5 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 6495.0964 | 20 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 11.6346 | Not meassured | Not meassured | Not meassured | 0.0917 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.0478 | Not meassured | Not meassured | 0.6015 | Not meassured | Not meassured | Not meassured | Not meassured | 18.3927 | Not meassured | Not meassured | 0.066 | 0.839 | Not meassured | Not meassured | 142.3505 | 0.05 | 21.714 | 0.25 | 0.36358 | 0.5 | 1.6721 | 3.6223 | 0.05 | 0.59192 | 0.25 | 0.5 | 0.25 | 0.5 | 0.12596 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-23 | CV | MRT | SW | CL | not given | 8.35 | 64.22 | 17.9 | not measured | 1.31 | 0.98 | not measured | 1.14 | 0.95 | not measured | not measured | 51.36 | 6.61 | 100000 | 5 | 5 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 11.3763 | Not meassured | Not meassured | Not meassured | 0.0635 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.0446 | Not meassured | Not meassured | 0.6151 | Not meassured | Not meassured | Not meassured | Not meassured | 18.1996 | Not meassured | Not meassured | 0.059 | 0.802 | Not meassured | Not meassured | 132.4177 | 0.05 | 18.9715 | 0.25 | 0.2831 | 0.5 | 1.2553 | 3.1691 | 0.05 | 0.55213 | 0.25 | 0.5 | 0.25 | 0.5 | 0.1042 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-23 | CV | TANK | SW | CL | not given | 7.68 | 63.86 | 17.7 | not measured | 1.29 | 1.08 | not measured | 1.17 | 0.82 | not measured | not measured | 68.48 | 6.79 | 7500 | 5 | 5 | 1000 | 5 | positive | Not tested | no result | no result | no result | 84 | 80 | 20 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 11.2796 | Not meassured | Not meassured | Not meassured | 0.2989 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.1086 | Not meassured | Not meassured | 0.6387 | Not meassured | Not meassured | Not meassured | Not meassured | 20.0384 | Not meassured | Not meassured | 0.113 | 0.739 | Not meassured | Not meassured | 112.351 | 0.05 | 19.5953 | 0.25 | 0.29633 | 0.5 | 1.289 | 3.1694 | 0.05 | 0.52371 | 0.25 | 0.5 | 0.25 | 0.5 | 0.12351 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-23 | CV | TCR | SW | CL | not given | 7.86 | 68 | 20 | not measured | 1.7 | 1.35 | not measured | 1.23 | 1 | not measured | not measured | 51.36 | 6.62 | 35000 | 5 | 5 | 1000 | 2.5 | negative | Not tested | no result | no result | no result | 84 | 80 | 20 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 11.3041 | Not meassured | Not meassured | Not meassured | 0.2305 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.0781 | Not meassured | Not meassured | 0.6124 | Not meassured | Not meassured | Not meassured | Not meassured | 19.2132 | Not meassured | Not meassured | 0.091 | 0.7 | Not meassured | Not meassured | 21.4084 | 0.05 | 2.3359 | 0.25 | 1.737 | 0.5 | 0.47468 | 0.40873 | 0.05 | 0.077214 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-23 | CV | DBP | SW | CL | not given | 7.93 | 69.26 | 20.7 | not measured | 1.35 | 1.24 | not measured | 1.15 | 0.77 | not measured | not measured | 51.36 | 6.79 | 35000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 11.4299 | Not meassured | Not meassured | Not meassured | 0.1644 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.0457 | Not meassured | Not meassured | 0.5939 | Not meassured | Not meassured | Not meassured | Not meassured | 18.3089 | Not meassured | Not meassured | 0.063 | 0.747 | Not meassured | Not meassured | 109.6206 | 0.05 | 18.2948 | 0.25 | 0.23544 | 0.5 | 1.2298 | 2.9967 | 0.05 | 0.49492 | 0.25 | 0.5 | 0.25 | 0.5 | 0.10408 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-23 | CV | SW | SW | CL | not given | 7.57 | 67.28 | 19.6 | not measured | 0 | 0 | not measured | 0 | 0 | not measured | not measured | 68.48 | 7.09 | 3050000 | 3760 | 50 | 10000 | not done | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 4824755.7681 | 24.3697 | 24.0021 | 4246 | 436 | 75 | 32 | 44 | 16 | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 8.1274 | Not meassured | Not meassured | Not meassured | 0.0687 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | -0.006 | Not meassured | Not meassured | -0.011 | Not meassured | Not meassured | Not meassured | Not meassured | 2.0487 | Not meassured | Not meassured | 0.156 | 1.684 | Not meassured | Not meassured | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CV | EP | SW | CL | not given | 7.61 | 73.22 | 22.9 | 0.008 | 2.14 | 1.97 | not measured | 1.78 | 1.67 | not measured | not measured | 68.48 | 5.99 | 65000 | 0 | 0 | 1000 | 3 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | -0.004 | -0.004 | 0.0161 | -0.005 | -0.008 | 16.17 | -0.0003 | 10.763 | -0.001 | 0.0055 | 0.0056 | 0.7662 | 2.669 | -0.005 | 1.602 | -0.001 | 9.06 | -0.001 | 0.0731 | 0.0376 | Not meassured | -0.002 | 0.698 | 0.7304 | -0.003 | 4.181 | -0.001 | 24.2679 | 0.0422 | 8.215 | 0.066 | 0.665 | -0.001 | 0.0054 | 24.2669 | 0.05 | 5.4785 | 0.25 | 0.11388 | 0.5 | 0.05 | 1.0908 | 0.05 | 0.093731 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CV | MP | SW | CL | not given | 7.68 | 73.04 | 22.8 | 0.006 | 1.1 | 1.02 | not measured | 0.97 | 0.84 | not measured | not measured | 85.6 | 6.1 | 15000 | 5 | 5 | 1000 | 5 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0237 | -0.004 | 0.0204 | -0.005 | -0.008 | 17.93 | -0.0003 | 10.7384 | -0.001 | 0.005 | 0.0098 | 0.7675 | 2.417 | -0.005 | 1.405 | -0.001 | 9.06 | -0.001 | 0.1022 | -0.006 | Not meassured | -0.002 | 0.6952 | 0.6873 | -0.003 | 4.243 | -0.001 | 25.2574 | 0.0426 | 8.509 | 0.07 | 0.788 | -0.001 | 0.0053 | 53.4281 | 0.05 | 8.0356 | 0.25 | 0.05 | 0.5 | 0.11396 | 1.4369 | 0.05 | 0.18924 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CV | MRT | SW | CL | not given | 7.71 | 75.2 | 24 | 0.006 | 1.19 | 1 | not measured | 1.15 | 1.02 | not measured | not measured | 85.6 | 6.22 | 5000 | 5 | 5 | 1000 | 3 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.1469 | -0.004 | 0.0236 | -0.005 | -0.008 | 17.58 | -0.0003 | 10.4675 | -0.001 | -0.001 | 0.2611 | 0.7282 | 2.481 | -0.005 | 1.781 | 0.0586 | 8.894 | -0.001 | 0.077 | 0.0257 | Not meassured | -0.002 | 0.5634 | 0.7705 | -0.003 | 4.271 | -0.001 | 24.5985 | 0.0445 | 8.287 | 0.062 | 0.818 | -0.001 | 0.0242 | 46.4766 | 0.05 | 7.0164 | 0.25 | 0.05 | 0.5 | 0.05 | 1.2625 | 0.05 | 0.18586 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CV | TANK | SW | CL | not given | 6.63 | 74.84 | 23.8 | 0.006 | 1.12 | 1.02 | not measured | 1.04 | 0.92 | not measured | not measured | 68.48 | 6.04 | 60000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0256 | -0.004 | 0.0195 | -0.005 | -0.008 | 17.86 | -0.0003 | 10.3558 | -0.001 | 0.0012 | 0.0041 | 0.7211 | 2.504 | -0.005 | 1.487 | -0.001 | 8.778 | -0.001 | 0.105 | 0.0578 | Not meassured | -0.002 | 0.6841 | 0.7031 | -0.003 | 4.297 | -0.001 | 27.5425 | 0.0429 | 9.242 | 0.084 | 0.782 | -0.001 | 0.0032 | 38.21 | 0.05 | 5.8203 | 0.25 | 0.05 | 0.5 | 0.10127 | 0.98742 | 0.05 | 0.1348 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CV | TCR | SW | CL | not given | 7.66 | 80.78 | 27.1 | 0.006 | 1.43 | 1.34 | not measured | 1.23 | 1.08 | not measured | not measured | 68.48 | 6.08 | 17500 | 5 | 5 | 1000 | 4 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0261 | -0.004 | 0.0185 | -0.005 | -0.008 | 17.59 | -0.0003 | 10.5513 | -0.001 | 0.0061 | 0.0118 | 0.7135 | 2.478 | -0.005 | 1.486 | 0.0032 | 8.92 | -0.001 | -0.005 | 0.0309 | Not meassured | -0.002 | 0.7424 | 0.6897 | -0.003 | 4.201 | -0.001 | 24.6231 | 0.0432 | 8.346 | 0.067 | 0.799 | -0.001 | 0.0044 | 47.9782 | 0.05 | 7.4575 | 0.25 | 0.05 | 0.5 | 0.14788 | 1.331 | 0.05 | 0.16603 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CV | DBP | SW | CL | not given | 7.69 | 80.6 | 27 | 0.006 | 1.48 | 1.34 | not measured | 1.35 | 1.15 | not measured | not measured | 68.48 | 6.02 | 5000 | 5 | 5 | 1000 | 1.5 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0149 | -0.004 | 0.0202 | -0.005 | -0.008 | 17.67 | -0.0003 | 10.3959 | -0.001 | 0.0013 | 0.0249 | 0.7366 | 2.465 | -0.005 | 1.412 | -0.001 | 9.066 | -0.001 | 0.0719 | 0.0207 | Not meassured | -0.002 | 0.7763 | 0.687 | -0.003 | 4.277 | -0.001 | 24.3714 | 0.0414 | 8.378 | 0.064 | 0.821 | -0.001 | 0.0049 | 43.6434 | 0.05 | 7.6649 | 0.25 | 0.05 | 0.5 | 0.13488 | 1.3259 | 0.05 | 0.19507 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CV | SW | SW | CL | not given | 7.91 | 72.5 | 22.5 | 0.003 | 0 | 0 | not measured | 0 | 0 | not measured | not measured | 51.36 | 7.1 | 192500000 | 5200 | 50 | 10000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 552130.27 | 27.2445 | 26.974 | 4246 | 7587.8865 | 1816.8039 | 32 | 44 | 16 | -0.004 | -0.004 | 0.0191 | -0.005 | -0.008 | 6.343 | -0.0003 | 6.623 | -0.001 | 0.002 | 0.1463 | 0.0899 | 2.482 | -0.005 | 1.56 | 0.1834 | 4.981 | -0.001 | 0.0865 | -0.006 | Not meassured | -0.002 | -0.011 | 0.0074 | -0.003 | 4.396 | -0.001 | 1.2355 | 0.0328 | 0.4793 | 0.178 | 2.134 | -0.001 | 0.0037 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-10 | CV | EP | SW | CL | not given | 6.33 | 48.02 | 8.9 | 0.011 | 1.55 | 1.47 | not measured | 1.48 | 1.31 | not measured | not measured | 68.48 | 7.53 | 12500 | 0 | 0 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 260.9042 | 35.7612 | 35.5377 | 40 | 22 | 8 | 32 | 44 | 16 | 0.0191 | 0.0045 | 0.0186 | -0.005 | -0.008 | 18.47 | -0.0003 | 11.0246 | -0.001 | 0.0032 | 0.0036 | 0.685 | 2.497 | -0.005 | 1.699 | -0.001 | 8.598 | -0.001 | 0.0111 | 0.0367 | Not meassured | -0.002 | 0.6261 | 0.7077 | -0.003 | 4.039 | -0.001 | 28.8844 | 0.0485 | 10.43 | 0.09 | 0.658 | -0.001 | 0.0045 | 22.0266 | 0.05 | 4.7172 | 0.25 | 0.05 | 0.5 | 0.17488 | 0.77697 | 0.05 | 0.091971 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-10 | CV | MP | SW | CL | not given | 6.25 | 55.4 | 13 | not measured | 1.12 | 1.1 | not measured | 0.97 | 0.86 | not measured | not measured | 85.6 | 7.66 | 120000 | 5 | 5 | 1000 | 1.5 | negative | Not tested | no result | no result | no result | 84 | 1726.7089 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0144 | -0.004 | 0.0182 | -0.005 | -0.008 | 19.88 | -0.0003 | 11.1782 | -0.001 | 0.0042 | 0.0135 | 0.6264 | 2.655 | -0.005 | 1.622 | -0.001 | 8.563 | -0.001 | 0.0118 | 0.0326 | Not meassured | -0.002 | 0.6035 | 0.6538 | -0.003 | 4.04 | -0.001 | 28.9887 | 0.0509 | 10.67 | 0.081 | 0.68 | -0.001 | 0.006 | 42.0127 | 0.05 | 6.4553 | 0.25 | 0.05 | 0.5 | 0.23171 | 0.96015 | 0.05 | 0.14726 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-10 | CV | MRT | SW | CL | not given | 6.38 | 51.8 | 11 | 0.005 | 1.24 | 1.21 | not measured | 1.18 | 1.15 | not measured | not measured | 68.48 | 7.73 | 22500 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0746 | -0.004 | 0.0194 | -0.005 | -0.008 | 19.11 | -0.0003 | 11.2027 | -0.001 | -0.001 | 0.105 | 0.6926 | 2.536 | -0.005 | 1.744 | 0.018 | 8.713 | -0.001 | 0.0097 | 0.0401 | Not meassured | -0.002 | 0.5824 | 0.663 | -0.003 | 4.016 | -0.001 | 28.8729 | 0.0486 | 10.48 | 0.085 | 0.655 | -0.001 | 0.0094 | 31.9645 | 0.05 | 5.4615 | 0.25 | 0.05 | 0.5 | 0.22622 | 0.92169 | 0.05 | 0.12684 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-10 | CV | TANK | SW | CL | not given | 6.47 | 49.64 | 9.8 | 0.006 | 1.2 | 1.1 | not measured | 1.12 | 1.02 | not measured | not measured | 68.48 | 7.61 | 25000 | 5 | 5 | 1000 | Bacillus/Mold | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | -0.004 | -0.004 | 0.0198 | -0.005 | -0.008 | 19.59 | -0.0003 | 11.3379 | -0.001 | 0.001 | 0.0031 | 0.6671 | 2.717 | -0.005 | 1.757 | -0.001 | 8.978 | 0.001 | 0.0137 | 0.0256 | Not meassured | -0.002 | 0.6233 | 0.6759 | -0.003 | 4.153 | -0.001 | 28.9194 | 0.0524 | 10.63 | 0.074 | 0.735 | -0.001 | 0.0045 | 28.6225 | 0.05 | 5.2799 | 0.25 | 0.05 | 0.5 | 0.13865 | 0.91798 | 0.05 | 0.14173 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-10 | CV | TCR | SW | CL | not given | 6.45 | 57.2 | 14 | not measured | 1.23 | 1.16 | not measured | 1.09 | 1 | not measured | not measured | 68.48 | 7.79 | 10000 | 5 | 5 | 1000 | 2 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0151 | -0.004 | 0.0188 | -0.005 | -0.008 | 19.58 | -0.0003 | 11.2965 | -0.001 | 0.0069 | 0.0063 | 0.6674 | 2.473 | -0.005 | 1.627 | -0.001 | 8.725 | -0.001 | 0.0155 | 0.0389 | Not meassured | -0.002 | 0.6093 | 0.6316 | -0.003 | 4.02 | -0.001 | 28.9644 | 0.0509 | 10.4 | 0.086 | 0.683 | -0.001 | 0.0041 | 34.796 | 0.05 | 5.836 | 0.25 | 0.05 | 0.5 | 0.2017 | 1.0118 | 0.05 | 0.13362 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-10 | CV | DBP | SW | CL | not given | 6.51 | 55.4 | 13 | 0.003 | 1.33 | 1.24 | not measured | 1.22 | 1.14 | not measured | not measured | 68.48 | 7.75 | 112500 | 5 | 5 | 1000 | 1.5 | negative | Not tested | no result | no result | no result | 84 | 1611.9265 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0375 | -0.004 | 0.0193 | -0.005 | -0.008 | 18.62 | -0.0003 | 11.1596 | -0.001 | -0.001 | 0.0367 | 0.6698 | 2.308 | -0.005 | 1.702 | 0.0014 | 8.771 | -0.001 | 0.0147 | 0.0339 | Not meassured | -0.002 | 0.5819 | 0.6408 | -0.003 | 4.054 | -0.001 | 28.9047 | 0.0502 | 10.37 | 0.086 | 0.602 | -0.001 | 0.0049 | 20.2707 | 0.05 | 4.1864 | 0.25 | 0.05 | 0.5 | 0.10263 | 0.77522 | 0.05 | 0.094906 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-10 | CV | SW | SW | CL | not given | 6.44 | 41.9 | 5.5 | 0.007 | 0 | 0 | not measured | 0 | 0 | not measured | not measured | 68.48 | 7.62 | 4200000 | 2430 | 3000 | 35000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 951056.5392 | 25.0267 | 27.1708 | 4246 | 871.2333 | 2951.3929 | 32 | 44 | 16 | 0.0197 | -0.004 | 0.0225 | -0.005 | -0.008 | 6.568 | -0.0003 | 8.077 | -0.001 | -0.001 | 0.2948 | 0.0648 | 2.323 | -0.005 | 1.651 | 0.0476 | 5.459 | -0.001 | 0.0103 | 0.0484 | Not meassured | -0.002 | -0.011 | 0.0059 | -0.003 | 4.5 | -0.001 | 1.7266 | 0.0378 | 0.6125 | 0.227 | 1.617 | -0.001 | 0.0014 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | CZ | EP | SW | CL | not given | 7.96 | 42.44 | 5.8 | 0.007 | 1.42 | 1.37 | not measured | 1.19 | 1 | not measured | not measured | 51.36 | 8.88 | 5000 | 5 | 5 | 1000 | 0 | negative | 10000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0137 | -0.004 | 0.0232 | -0.005 | -0.008 | 13.67 | -0.0003 | 10.6069 | -0.001 | 0.0022 | 0.0092 | 0.7023 | 2.557 | -0.005 | 1.723 | 0.0143 | 9.805 | 0.0012 | -0.005 | 0.1521 | Not meassured | -0.002 | 0.954 | 0.9558 | -0.003 | 5.556 | -0.001 | 21.7437 | 0.0341 | 7.315 | 0.126 | 0.826 | -0.001 | 0.0035 | 18.3929 | 0.05 | 3.6986 | 0.25 | 0.23981 | 0.5 | 0.12054 | 0.54211 | 0.05 | 0.085821 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | CZ | MP | SW | CL | not given | 8.04 | 47.3 | 8.5 | not measured | 0.85 | 0.81 | not measured | 0.83 | 0.75 | not measured | not measured | 51.36 | 9.21 | 5000 | 5 | 5 | 1000 | 0 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0157 | -0.004 | 0.0198 | -0.005 | -0.008 | 14.32 | -0.0003 | 10.6844 | -0.001 | 0.002 | 0.0069 | 0.713 | 2.601 | -0.005 | 1.671 | 0.0091 | 9.802 | -0.001 | -0.005 | 0.1732 | Not meassured | -0.002 | 1 | 0.9447 | -0.003 | 5.401 | -0.001 | 22.1953 | 0.0351 | 7.487 | 0.133 | 0.746 | -0.001 | 0.0042 | 20.295 | 0.05 | 4.2069 | 0.25 | 0.14695 | 0.5 | 0.13054 | 0.88138 | 0.05 | 0.084064 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | CZ | MRT | SW | CL | not given | 6.06 | 47.12 | 8.4 | 0.005 | 0.94 | 0.88 | not measured | 0.91 | 0.8 | not measured | not measured | 51.36 | 8.25 | 140000 | 5 | 5 | 1000 | 0 | negative | 70000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 142.9307 | 33.8043 | 34.7238 | 40 | 22 | 3092.2589 | 32 | 44 | 16 | 0.0132 | -0.004 | 0.0208 | -0.005 | -0.008 | 14.3 | -0.0003 | 10.5461 | -0.001 | 0.0024 | 0.0142 | 0.6902 | 2.635 | -0.005 | 1.686 | 0.0121 | 9.823 | -0.001 | -0.005 | 0.1486 | Not meassured | -0.002 | 0.9456 | 0.9201 | -0.003 | 5.525 | -0.001 | 21.0358 | 0.0356 | 7.143 | 0.11 | 0.727 | -0.001 | 0.0103 | 15.4401 | 0.05 | 3.3402 | 0.25 | 0.17219 | 0.5 | 0.05 | 0.69437 | 0.05 | 0.08318 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | CZ | TANK | SW | CL | not given | 8.03 | 45.5 | 7.5 | 0.005 | 0.61 | 0.53 | not measured | 0.75 | 0.67 | not measured | not measured | 51.36 | 8.9 | 5000 | 5 | 5 | 1000 | 0 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 286.6087 | 37.5735 | 36.3126 | 119.5955 | 22 | 683.5125 | 32 | 44 | 16 | 0.0209 | -0.004 | 0.0198 | -0.005 | -0.008 | 14.53 | -0.0003 | 10.7844 | -0.001 | 0.0043 | 0.0065 | 0.7157 | 2.651 | -0.005 | 1.721 | 0.0082 | 10.18 | -0.001 | -0.005 | 0.2087 | Not meassured | -0.002 | 0.9751 | 0.9574 | -0.003 | 5.377 | -0.001 | 22.9596 | 0.0363 | 7.893 | 0.197 | 0.891 | -0.001 | 0.0088 | 21.3223 | 0.05 | 4.391 | 0.25 | 0.15309 | 0.5 | 0.13192 | 0.90484 | 0.05 | 0.085153 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | CZ | TCR | SW | CL | not given | 8.23 | 46.76 | 8.2 | 0.006 | 0.63 | 0.58 | not measured | 0.68 | 0.6 | not measured | not measured | 51.36 | 8.64 | 5000 | 5 | 5 | 1000 | 0 | negative | 10000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.019 | -0.004 | 0.0182 | -0.005 | -0.008 | 14.56 | -0.0003 | 10.82 | -0.001 | 0.0035 | 0.0068 | 0.7394 | 2.606 | -0.005 | 1.649 | 0.0076 | 9.985 | -0.001 | -0.005 | 0.1991 | Not meassured | -0.002 | 1.0208 | 0.944 | -0.003 | 5.245 | -0.001 | 23.0237 | 0.0359 | 7.74 | 0.183 | 0.88 | -0.001 | 0.005 | 22.2613 | 0.05 | 4.1984 | 0.25 | 0.19048 | 0.5 | 0.12624 | 0.76932 | 0.05 | 0.064515 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | CZ | DBP | SW | CL | not given | 8.26 | 45.32 | 7.4 | 0.008 | 0.9 | 0.85 | not measured | 0.9 | 0.77 | not measured | not measured | 51.36 | 8.61 | 12500 | 5 | 5 | 1000 | 0 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0278 | -0.004 | 0.022 | -0.005 | -0.008 | 14.57 | -0.0003 | 10.6001 | -0.001 | 0.0011 | 0.0224 | 0.7069 | 2.744 | -0.005 | 1.774 | 0.0088 | 9.989 | 0.0011 | 0.097 | 0.168 | Not meassured | -0.002 | 0.9428 | 0.9459 | -0.003 | 5.505 | -0.001 | 22.1168 | 0.0355 | 7.617 | 0.13 | 0.729 | -0.001 | 0.009 | 15.5153 | 0.05 | 3.7209 | 0.25 | 0.18847 | 0.5 | 0.10828 | 0.70649 | 0.05 | 0.06631 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | CZ | SW | SW | CL | not given | 8.58 | 42.8 | 6 | 0.004 | 0 | 0 | not measured | 0.04 | 0.003 | not measured | not measured | 51.36 | 7.52 | 550000 | 12340 | 300 | 10000 | Bacillus | positive | 1000000 | No L colonies | Negative | Negative | 8421 | 23346.5 | 2039 | 1416 | 301808.6786 | 25.8508 | 36.6691 | 4246 | 83686.26 | 10213.7088 | 32 | 44 | 16 | 0.0201 | -0.004 | 0.0244 | -0.005 | -0.008 | 5.716 | -0.0003 | 4.4735 | -0.001 | 0.0126 | 1.221 | 0.0915 | 2.761 | -0.005 | 1.746 | 0.1481 | 4.259 | -0.001 | 0.0853 | 0.4062 | Not meassured | -0.002 | -0.011 | 0.0327 | -0.003 | 5.829 | -0.001 | 2.6226 | 0.0259 | 1.032 | 0.929 | 3.465 | -0.001 | 0.0026 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-22 | CZ | EP | SW | CL | not given | 7.63 | 66.2 | 19 | not measured | 1.91 | 1.56 | not measured | 1.59 | 1.31 | not measured | not measured | 68.48 | 6.6 | 5000 | 5 | 0 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 10.6875 | Not meassured | Not meassured | Not meassured | 0.7303 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.2828 | Not meassured | Not meassured | 0.9099 | Not meassured | Not meassured | Not meassured | Not meassured | 23.0988 | Not meassured | 9999999999999990 | 0.296 | 0.714 | Not meassured | Not meassured | 61.0711 | 0.05 | 14.8014 | 0.25 | 0.36363 | 0.5 | 0.59715 | 3.117 | 0.05 | 0.42098 | 0.25 | 0.5 | 0.25 | 0.5 | 0.19371 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-22 | CZ | MP | SW | CL | not given | 7.96 | 65.48 | 18.6 | not measured | 1.03 | 0.97 | not measured | 0.89 | 0.83 | not measured | not measured | 68.48 | 6.78 | 110000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 2411.2096 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 11.0946 | Not meassured | Not meassured | Not meassured | 0.6967 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.3492 | Not meassured | Not meassured | 0.8939 | Not meassured | Not meassured | Not meassured | Not meassured | 23.961 | Not meassured | 9999999999999990 | 0.355 | 0.785 | Not meassured | Not meassured | 107.1928 | 0.05 | 19.2241 | 0.25 | 0.33958 | 0.5 | 0.88342 | 4.0916 | 0.05 | 0.50442 | 0.25 | 0.5 | 0.25 | 0.5 | 0.17146 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-22 | CZ | MRT | SW | CL | not given | 7.9 | 65.3 | 18.5 | not measured | 1.12 | 1.09 | not measured | 1.04 | 0.84 | not measured | not measured | 68.48 | 6.81 | 22500 | 5 | 5 | 1000 | 2 | negative | Not tested | no result | no result | no result | 84 | 4 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 13.4335 | Not meassured | Not meassured | Not meassured | 0.6954 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.3257 | Not meassured | Not meassured | 0.8835 | Not meassured | Not meassured | Not meassured | Not meassured | 23.8977 | Not meassured | 9999999999999990 | 0.335 | 0.807 | Not meassured | Not meassured | 116.1223 | 0.05 | 22.5469 | 0.25 | 0.54596 | 0.5 | 1.3019 | 5.0013 | 0.05 | 0.56163 | 0.25 | 0.5 | 0.25 | 0.5 | 0.22083 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-22 | CZ | TANK | SW | CL | not given | 7.8 | 63.86 | 17.7 | not measured | 1.01 | 0.87 | not measured | 0.83 | 0.55 | not measured | not measured | 68.48 | 7.13 | 6000000 | 5 | 5 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 11.1608 | Not meassured | Not meassured | Not meassured | 0.6949 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0175 | 0.3652 | Not meassured | Not meassured | 0.9163 | Not meassured | Not meassured | Not meassured | Not meassured | 24.0954 | Not meassured | 9999999999999990 | 0.415 | 0.772 | Not meassured | Not meassured | 87.375 | 0.05 | 15.9912 | 0.25 | 0.16592 | 0.5 | 0.61762 | 3.259 | 0.05 | 0.40098 | 0.25 | 0.5 | 0.25 | 0.5 | 0.15563 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-22 | CZ | TCR | SW | CL | not given | 7.8 | 63.68 | 17.6 | not measured | 0.89 | 0.85 | not measured | 0.88 | 0.7 | not measured | not measured | 68.48 | 7.01 | 12500 | 5 | 5 | 1000 | 4.5 | negative | Not tested | no result | no result | no result | 84 | 4 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 11.1374 | Not meassured | Not meassured | Not meassured | 0.6942 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 0.017 | 0.368 | Not meassured | Not meassured | 0.8929 | Not meassured | Not meassured | Not meassured | Not meassured | 24.1172 | Not meassured | 9999999999999990 | 0.379 | 0.763 | Not meassured | Not meassured | 108.6343 | 0.05 | 18.8366 | 0.25 | 0.31875 | 0.5 | 1.0939 | 3.952 | 0.05 | 0.46533 | 0.25 | 0.5 | 0.25 | 0.5 | 0.16373 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-22 | CZ | DBP | SW | CL | not given | 8.05 | 65.84 | 18.8 | not measured | 0.95 | 0.92 | not measured | 0.95 | 0.84 | not measured | not measured | 68.48 | 7.32 | 6000000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 11.0244 | Not meassured | Not meassured | Not meassured | 0.6915 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0202 | 0.3462 | Not meassured | Not meassured | 0.8883 | Not meassured | Not meassured | Not meassured | Not meassured | 23.9808 | Not meassured | 9999999999999990 | 0.351 | 0.754 | Not meassured | Not meassured | 95.5098 | 0.05 | 17.1174 | 0.25 | 0.27577 | 0.5 | 0.90194 | 3.6221 | 0.05 | 0.42403 | 0.25 | 0.5 | 0.25 | 0.5 | 0.14624 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-04-22 | CZ | SW | SW | CL | not given | 8.04 | 65.12 | 18.4 | not measured | 0 | 0 | not measured | 0 | 0 | not measured | not measured | 68.48 | 7.61 | 5000000 | 7850 | 5 | 10000 | not done | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 656408.5049 | 27.2956 | 27.2566 | 4246 | 434 | 75 | 32 | 44 | 16 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 10.3068 | Not meassured | Not meassured | Not meassured | 0.0783 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0137 | 0.2614 | Not meassured | Not meassured | -0.011 | Not meassured | Not meassured | Not meassured | Not meassured | 2.2979 | Not meassured | 9999999999999990 | 0.526 | 3.018 | Not meassured | Not meassured | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CZ | EP | SW | CL | not given | 7.16 | 73.04 | 22.8 | 0.003 | 1.82 | 1.73 | not measured | 1.81 | 1.7 | not measured | not measured | 51.36 | 6.2 | 5000 | 5 | 5 | 1000 | 6 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0135 | -0.004 | 0.0195 | -0.005 | -0.008 | 13.23 | -0.0003 | 8.6705 | -0.001 | 0.0019 | 0.0075 | 0.7287 | 2.875 | -0.005 | 1.696 | -0.001 | 8.723 | -0.001 | 0.0678 | -0.006 | Not meassured | -0.002 | 1.0049 | 1.033 | -0.003 | 5.027 | -0.001 | 21.9934 | 0.0346 | 7.451 | 0.073 | 0.855 | -0.001 | 0.0042 | 21.6982 | 0.05 | 4.9307 | 0.25 | 0.05 | 0.5 | 0.13399 | 1.0645 | 0.05 | 0.12026 | 0.25 | 0.5 | 0.25 | 0.5 | 0.057665 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CZ | MP | SW | CL | not given | 7.35 | 77.9 | 25.5 | 0.009 | 1.04 | 0.94 | not measured | 1.1 | 0.91 | not measured | not measured | 68.48 | 6.5 | 7500 | 5 | 5 | 1000 | 25 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.007 | -0.004 | 0.0195 | -0.005 | -0.008 | 14.54 | -0.0003 | 9.294 | -0.001 | 0.0015 | 0.0047 | 0.6948 | 3.008 | -0.005 | 1.552 | -0.001 | 9.136 | 0.0015 | 0.1037 | -0.006 | Not meassured | -0.002 | 1.0631 | 1.015 | -0.003 | 5.101 | -0.001 | 22.1104 | 0.0367 | 7.534 | 0.082 | 0.954 | -0.001 | 0.0028 | 29.112 | 0.05 | 5.3374 | 0.25 | 0.05 | 0.5 | 0.3492 | 1.1686 | 0.05 | 0.12191 | 0.25 | 0.5 | 0.25 | 0.5 | 0.056284 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CZ | MRT | SW | CL | not given | 7.38 | 77.72 | 25.4 | 0.006 | 1.4 | 1.17 | not measured | 1.08 | 0.94 | not measured | not measured | 51.36 | 6.22 | 95000 | 5 | 5 | 1000 | 15 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0046 | -0.004 | 0.0192 | -0.005 | -0.008 | 14.43 | -0.0003 | 8.9868 | -0.001 | -0.001 | 0.009 | 0.6785 | 3 | -0.005 | 1.509 | -0.001 | 8.899 | -0.001 | 0.0703 | -0.006 | Not meassured | -0.002 | 1.0314 | 1 | -0.003 | 5.089 | -0.001 | 21.7459 | 0.0356 | 7.444 | 0.072 | 0.917 | -0.001 | 0.0051 | 17.157 | 0.05 | 3.8004 | 0.25 | 0.05 | 0.5 | 0.19188 | 1.0208 | 0.05 | 0.10829 | 0.25 | 0.5 | 0.25 | 0.5 | 0.061875 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CZ | TANK | SW | CL | not given | 7.04 | 76.82 | 24.9 | 0.007 | 1.18 | 0.92 | not measured | 0.93 | 0.74 | not measured | not measured | 51.36 | 6.06 | 950000 | 86 | 5 | 1000 | 4 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0057 | -0.004 | 0.0199 | -0.005 | -0.008 | 14.09 | -0.0003 | 9.6149 | -0.001 | 0.0016 | 0.0064 | 0.676 | 3.028 | -0.005 | 1.555 | -0.001 | 9.359 | -0.001 | 0.0791 | 0.023 | Not meassured | -0.002 | 0.9683 | 1.016 | -0.003 | 5.102 | -0.001 | 22.0856 | 0.0358 | 7.521 | 0.067 | 0.824 | -0.001 | 0.0042 | 23.506 | 0.05 | 4.5949 | 0.25 | 0.05 | 0.5 | 0.24986 | 1.052 | 0.05 | 0.10712 | 0.25 | 0.5 | 0.25 | 0.5 | 0.062021 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CZ | TCR | SW | CL | not given | 7.04 | 77.18 | 25.1 | 0.006 | 0.81 | 0.69 | not measured | 0.59 | 0.48 | not measured | not measured | 51.36 | 6.21 | 15000 | 5 | 5 | 1000 | 8 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0114 | -0.004 | 0.0196 | -0.005 | -0.008 | 14.68 | -0.0003 | 9.8322 | -0.001 | 0.002 | 0.0052 | 0.7004 | 2.976 | -0.005 | 1.46 | -0.001 | 9.316 | -0.001 | 0.0941 | 0.0431 | Not meassured | -0.002 | 0.9781 | 0.9865 | -0.003 | 5.052 | -0.001 | 22.1815 | 0.0377 | 7.506 | 0.077 | 0.903 | -0.001 | 0.0022 | 21.5975 | 0.05 | 4.3055 | 0.25 | 0.05 | 0.5 | 0.19601 | 1.0172 | 0.05 | 0.09847 | 0.25 | 0.5 | 0.25 | 0.5 | 0.054063 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CZ | DBP | SW | CL | not given | 7.35 | 77.18 | 25.1 | 0.006 | 1.68 | 1.34 | not measured | 1.36 | 1.12 | not measured | not measured | 51.36 | 6 | 30000 | 5 | 5 | 1000 | 23 | positive | Not tested | no result | no result | no result | 84 | 3574.5763 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | -0.004 | -0.004 | 0.0194 | -0.005 | -0.008 | 13.15 | -0.0003 | 8.8463 | -0.001 | 0.0014 | 0.0053 | 0.7485 | 3.094 | -0.005 | 1.642 | -0.001 | 8.893 | -0.001 | 0.1208 | -0.006 | Not meassured | -0.002 | 1.1733 | 1.185 | -0.003 | 5.039 | -0.001 | 21.6207 | 0.0341 | 7.293 | 0.074 | 0.932 | -0.001 | 0.0099 | 15.5311 | 0.05 | 3.6296 | 0.25 | 0.05 | 0.5 | 0.1521 | 0.93232 | 0.05 | 0.10131 | 0.25 | 0.5 | 0.25 | 0.5 | 0.058201 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-10 | CZ | SW | SW | CL | not given | 7.64 | 75.56 | 24.2 | 0.003 | 0.01 | 0.01 | not measured | 0.01 | 0.01 | not measured | not measured | 34.24 | 7.43 | 166500000 | 2000 | 500 | 10000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 1795455.6274 | 28.2137 | 29.311 | 4246 | 12830.6275 | 75 | 32 | 44 | 16 | -0.004 | -0.004 | 0.0204 | -0.005 | -0.008 | 5.428 | -0.0003 | 5.037 | -0.001 | 0.0185 | 0.1677 | 0.1048 | 2.984 | -0.005 | 1.66 | 0.0139 | 4.7 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | 0.007 | -0.003 | 5.168 | -0.001 | 2.4544 | 0.026 | 0.8594 | 0.238 | 3.337 | -0.001 | 0.002 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-11 | CZ | EP | SW | CL | not given | 6.74 | 46.04 | 7.8 | 0.005 | 1.66 | 1.52 | not measured | 1.57 | 1.37 | not measured | not measured | 68.48 | 7.47 | 30000 | 5 | 0 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0191 | -0.004 | 0.0276 | -0.005 | -0.008 | 17.41 | -0.0003 | 11.946 | -0.001 | -0.001 | 0.0065 | 0.6872 | 2.947 | -0.005 | 1.94 | 0.0069 | 10.98 | -0.001 | 0.0149 | 0.0455 | Not meassured | -0.002 | 0.992 | 1.009 | -0.003 | 4.295 | -0.001 | 26.4852 | 0.0462 | 9.612 | 0.102 | 0.798 | -0.001 | 0.0025 | 30.2901 | 0.05 | 5.3036 | 0.25 | 0.15277 | 0.5 | 0.10307 | 0.95905 | 0.05 | 0.12258 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-11 | CZ | MP | SW | CL | not given | 6.72 | 54.14 | 12.3 | 0.005 | 1.17 | 1 | not measured | 1.12 | 0.89 | not measured | not measured | 68.48 | 7.85 | 70000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 4522.8104 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0262 | -0.004 | 0.0252 | -0.005 | -0.008 | 18.06 | -0.0003 | 12.8042 | -0.001 | 0.0011 | 0.0098 | 0.6813 | 2.944 | -0.005 | 1.859 | 0.0016 | 11.44 | -0.001 | 0.012 | 0.0405 | Not meassured | -0.002 | 0.9716 | 1.049 | -0.003 | 4.425 | -0.001 | 25.8281 | 0.0479 | 9.36 | 0.113 | 0.885 | -0.001 | 0.0044 | 45.0769 | 0.05 | 5.6814 | 0.25 | 0.10564 | 0.5 | 0.19566 | 0.96054 | 0.05 | 0.10652 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-11 | CZ | MRT | SW | CL | not given | 6.68 | 52.34 | 11.3 | 0.006 | 1.3 | 1.22 | not measured | 1.31 | 0.89 | not measured | not measured | 68.48 | 8.09 | 7500 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 381.0904 | 36.4501 | 36.4001 | 40 | 22 | 8 | 32 | 44 | 16 | -0.004 | -0.004 | 0.0259 | -0.005 | -0.008 | 18.08 | -0.0003 | 12.9403 | -0.001 | -0.001 | 0.0146 | 0.6846 | 2.848 | -0.005 | 1.873 | 0.0033 | 11.42 | -0.001 | 0.0081 | 0.0455 | Not meassured | -0.002 | 1.0025 | 1.076 | -0.003 | 4.296 | -0.001 | 26.2891 | 0.0476 | 9.596 | 0.108 | 0.715 | -0.001 | 0.0066 | 52.4189 | 0.05 | 6.7175 | 0.25 | 0.05 | 0.5 | 0.14644 | 1.158 | 0.05 | 0.11142 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-11 | CZ | TANK | SW | CL | not given | 6.67 | 50 | 10 | 0.005 | 1.13 | 1.05 | not measured | 1.1 | 0.88 | not measured | not measured | 68.48 | 7.75 | 125000 | 5 | 5 | 1000 | 1.5 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0437 | -0.004 | 0.028 | -0.005 | -0.008 | 17.17 | -0.0003 | 12.3876 | -0.001 | -0.001 | 0.0099 | 0.6776 | 2.922 | -0.005 | 1.901 | 0.0014 | 11.37 | -0.001 | 0.0197 | 0.034 | Not meassured | -0.002 | 0.9915 | 1.049 | -0.003 | 4.83 | -0.001 | 25.1045 | 0.0487 | 9.128 | 0.088 | 0.739 | -0.001 | 0.0055 | 46.5123 | 0.05 | 5.9195 | 0.25 | 0.05 | 0.5 | 0.18508 | 0.98955 | 0.05 | 0.098669 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-11 | CZ | TCR | SW | CL | not given | 6.62 | 53.78 | 12.1 | 0.006 | 1 | 0.92 | not measured | 0.97 | 0.59 | not measured | not measured | 68.48 | 8.38 | 30000 | 5 | 5 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0377 | -0.004 | 0.0253 | -0.005 | -0.008 | 17.09 | -0.0003 | 12.7875 | -0.001 | 0.002 | 0.0083 | 0.6767 | 2.821 | -0.005 | 1.798 | 0.0019 | 11.1 | -0.001 | 0.0208 | 0.0367 | Not meassured | -0.002 | 0.9574 | 0.9927 | -0.003 | 4.415 | -0.001 | 25.566 | 0.0486 | 8.827 | 0.092 | 0.717 | -0.001 | 0.0044 | 56.1925 | 0.05 | 6.4776 | 0.25 | 0.05 | 0.5 | 0.14626 | 1.0779 | 0.05 | 0.094862 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-11 | CZ | DBP | SW | CL | not given | 6.64 | 50.9 | 10.5 | 0.006 | 1.39 | 1.22 | not measured | 1.38 | 1.11 | not measured | not measured | 68.48 | 8.83 | 5000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0125 | -0.004 | 0.0256 | -0.005 | -0.008 | 17.12 | -0.0003 | 12.3747 | -0.001 | 0.0015 | 0.0109 | 0.6805 | 2.877 | -0.005 | 1.844 | 0.001 | 10.77 | -0.001 | 0.0157 | 0.0443 | Not meassured | -0.002 | 0.972 | 1.03 | -0.003 | 4.18 | -0.001 | 26.4214 | 0.045 | 9.368 | 0.1 | 0.723 | -0.001 | 0.0122 | 35.6525 | 0.05 | 5.5738 | 0.25 | 0.1156 | 0.5 | 0.20458 | 0.98217 | 0.05 | 0.098065 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-11 | CZ | SW | SW | CL | not given | 7.34 | 43.7 | 6.5 | 0.006 | 0 | 0 | not measured | 0 | 0 | not measured | not measured | 42.8 | 7.12 | 11850000 | 750 | 5 | 180000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 131585.5659 | 33.4185 | 30.619 | 4246 | 16795.914 | 75 | 32 | 44 | 16 | 0.0139 | -0.004 | 0.0298 | -0.005 | -0.008 | 6.615 | -0.0003 | 5.6622 | -0.001 | 0.0206 | 2.42 | 0.0848 | 2.942 | -0.005 | 1.853 | 0.4188 | 4.858 | -0.001 | 0.0081 | 0.0571 | Not meassured | -0.002 | -0.011 | 0.0148 | -0.003 | 4.339 | -0.001 | 1.8659 | 0.0347 | 0.7017 | 0.735 | 3.222 | 0.001 | 0.0017 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-11 | AA | EP | SW | CL | not given | 7.1 | 52.16 | 11.2 | 0.005 | 2.3 | 2.1 | not measured | 2.52 | 2.38 | not measured | not measured | 136.96 | 9.21 | 35000 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0509 | -0.004 | 0.0202 | -0.005 | -0.008 | 42.21 | -0.0003 | 16.7612 | -0.001 | 0.0018 | 0.0137 | 0.6354 | 1.385 | -0.005 | 9.931 | 0.006 | 7.074 | -0.001 | -0.005 | 1.3938 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 2.608 | -0.001 | 6.5122 | 0.0611 | 2.239 | 1.313 | 0.739 | -0.001 | 0.0016 | 16.0731 | 0.05 | 4.0724 | 0.25 | 0.28899 | 0.5 | 0.11452 | 0.7817 | 0.05 | 0.061707 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-11 | AA | MP | SW | CL | not given | 7 | 51.44 | 10.8 | not measured | 2.3 | 2.1 | not measured | 2.44 | 2.62 | not measured | not measured | 154.08 | 9.33 | 55000 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0333 | -0.004 | 0.0219 | -0.005 | -0.008 | 42.44 | -0.0003 | 21.0645 | -0.001 | 0.002 | 0.0033 | 0.5413 | 1.365 | -0.005 | 9.164 | -0.001 | 9.135 | -0.001 | -0.005 | 1.2711 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 2.332 | -0.001 | 7.0479 | 0.066 | 2.416 | 1.15 | 0.811 | -0.001 | 0.0035 | 28.7164 | 0.05 | 4.1469 | 0.25 | 0.36718 | 0.5 | 0.18005 | 0.52009 | 0.05 | 0.046975 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-11 | AA | MRT | SW | CL | not given | 7.12 | 51.62 | 10.9 | 0.006 | 1.7 | 1.5 | not measured | 1.62 | 1.5 | not measured | not measured | 154.08 | 9.19 | 50000 | 5 | 5 | 1000 | Bacillus | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0419 | -0.004 | 0.0228 | -0.005 | -0.008 | 49.33 | -0.0003 | 16.0035 | -0.001 | 0.0033 | 0.0019 | 0.4716 | 1.472 | -0.005 | 12.38 | -0.001 | 7.301 | -0.001 | -0.005 | 0.9811 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 1.766 | -0.001 | 7.4671 | 0.0771 | 2.569 | 0.901 | 1.003 | -0.001 | 0.0012 | 39.4989 | 0.05 | 4.2364 | 0.25 | 0.22259 | 0.5 | 0.11894 | 0.45708 | 0.05 | 0.045522 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-11 | AA | TANK | SW | CL | not given | 6.92 | 51.44 | 10.8 | 0.006 | 2 | 1.8 | not measured | 1.64 | 1.55 | not measured | not measured | 136.96 | 9.72 | 55000 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0416 | -0.004 | 0.0225 | -0.005 | -0.008 | 48.89 | -0.0003 | 15.9683 | -0.001 | 0.0012 | -0.001 | 0.4226 | 1.468 | -0.005 | 12.09 | 0.0023 | 7.33 | -0.001 | -0.005 | 1.0011 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 1.784 | -0.001 | 7.2659 | 0.0764 | 2.552 | 0.934 | 0.846 | -0.001 | 0.0027 | 38.7885 | 0.05 | 4.2297 | 0.25 | 0.26005 | 0.5 | 0.14428 | 0.46469 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-11 | AA | TCR | SW | CL | not given | 7.2 | 51.62 | 10.9 | not measured | 2 | 1.9 | not measured | 1.77 | 1.59 | not measured | not measured | 136.96 | 9.09 | 70000 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0302 | -0.004 | 0.0216 | -0.005 | -0.008 | 40.08 | -0.0003 | 20.086 | -0.001 | 0.0107 | -0.001 | 0.6649 | 1.489 | -0.005 | 8.657 | -0.001 | 8.319 | -0.001 | -0.005 | 1.3773 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 2.507 | -0.001 | 6.8072 | 0.0631 | 2.374 | 1.208 | 0.807 | -0.001 | 0.0093 | 26.8091 | 0.05 | 4.0669 | 0.25 | 0.44109 | 0.5 | 0.20365 | 0.51951 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-11 | AA | DBP | SW | CL | not given | 7.24 | 51.44 | 10.8 | not measured | 1.75 | 1.94 | not measured | 1.72 | 1.52 | not measured | not measured | 136.96 | 9.35 | 65000 | 5 | 5 | 1000 | Bacillus | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0364 | -0.004 | 0.0309 | -0.005 | -0.008 | 47.96 | -0.0003 | 18.5485 | -0.001 | 0.0029 | 0.0028 | 0.2281 | 1.633 | -0.005 | 12.61 | -0.001 | 8.113 | -0.001 | -0.005 | 1.1581 | Not meassured | -0.002 | -0.011 | 0.0687 | -0.003 | 2.141 | -0.001 | 9.3802 | 0.0934 | 3.277 | 1.069 | 1.162 | -0.001 | 0.0021 | 35.0999 | 0.05 | 5.1048 | 0.25 | 0.32126 | 0.5 | 0.17152 | 0.7409 | 0.05 | 0.065579 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-11 | AA | SW | SW | CL | not given | 6.95 | 57.38 | 14.1 | 0.007 | 0 | 0 | not measured | 0.09 | 0.08 | not measured | not measured | 119.84 | 8.9 | 60000000 | 1480 | 50 | 10000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 833403.097 | Inhibition | 26.1052 | 108325.2333 | 68261.0766 | 12211.3859 | 32 | 44 | 16 | 0.1001 | -0.004 | 0.0225 | -0.005 | -0.008 | 43 | -0.0003 | 4.7759 | -0.001 | -0.001 | 0.1307 | 0.0674 | 1.388 | -0.005 | 10.24 | 0.0968 | 2.887 | -0.001 | -0.005 | 1.4148 | Not meassured | -0.002 | -0.011 | 0.0158 | -0.003 | 3.141 | -0.001 | 5.188 | 0.0626 | 1.791 | 1.308 | 1.018 | -0.001 | 0.0012 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-06-10 | AA | EP | SW | CL | not given | 6.93 | 68 | 20 | not measured | 2.2 | 1.84 | not measured | 1.85 | 1.56 | not measured | not measured | 119.84 | 6.35 | 5000 | 0 | 0 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0273 | Not meassured | Not meassured | 13.1286 | Not meassured | Not meassured | Not meassured | 0.4909 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.2754 | Not meassured | Not meassured | -0.011 | Not meassured | Not meassured | Not meassured | Not meassured | 12.6377 | Not meassured | Not meassured | 0.319 | 1.944 | Not meassured | Not meassured | 77.0602 | 0.05 | 16.5881 | 0.25 | 2.2634 | 0.5 | 1.024 | 2.3428 | 0.05 | 0.17015 | 0.25 | 0.5 | 0.25 | 0.5 | 0.084599 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-06-10 | AA | MP | SW | CL | not given | 6.63 | 68 | 20 | not measured | 1.75 | 1.48 | not measured | 1.2 | 1.05 | not measured | not measured | 102.72 | 6.62 | 5000 | 5 | 5 | 1000 | 3.5 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0193 | Not meassured | Not meassured | 12.3249 | Not meassured | Not meassured | Not meassured | 0.5032 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.3083 | Not meassured | Not meassured | -0.011 | Not meassured | Not meassured | Not meassured | Not meassured | 10.8197 | Not meassured | Not meassured | 0.342 | 1.897 | Not meassured | Not meassured | 152.5538 | 0.05 | 16.0064 | 0.25 | 1.6362 | 0.5 | 1.3917 | 1.8626 | 0.05 | 0.26027 | 0.25 | 0.5 | 0.25 | 0.5 | 0.068867 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-06-10 | AA | MRT | SW | CL | not given | 6.94 | 71.6 | 22 | 0.008 | 0.55 | 0.21 | not measured | 0.04 | 0.01 | not measured | not measured | 291.04 | 3.47 | 145000 | 5 | 5 | 1000 | 1.5 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0262 | Not meassured | Not meassured | 2.6739 | Not meassured | Not meassured | Not meassured | 0.1522 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | -0.006 | Not meassured | Not meassured | -0.011 | Not meassured | Not meassured | Not meassured | Not meassured | 12.256 | Not meassured | Not meassured | 0.327 | 3.145 | Not meassured | Not meassured | 1.2545 | 0.05 | 1.571 | 0.25 | 0.05 | 0.5 | 0.05 | 2.9539 | 0.05 | 0.06919 | 0.25 | 0.5 | 0.25 | 0.5 | 4.4639 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-06-10 | AA | TANK | SW | CL | not given | 7.46 | 68.18 | 20.1 | not measured | 1.4 | 0.9 | not measured | 1.42 | 1.09 | not measured | not measured | 119.84 | 6.67 | 120000 | 5 | 5 | 1000 | 5 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 12.0476 | Not meassured | Not meassured | Not meassured | 0.467 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.2808 | Not meassured | Not meassured | -0.011 | Not meassured | Not meassured | Not meassured | Not meassured | 12.3056 | Not meassured | Not meassured | 0.319 | 1.966 | Not meassured | Not meassured | 94.8516 | 0.05 | 15.9205 | 0.25 | 1.6714 | 0.5 | 0.91619 | 2.0303 | 0.05 | 0.3178 | 0.25 | 0.5 | 0.25 | 0.5 | 0.1384 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-06-10 | AA | TCR | SW | CL | not given | 7.54 | 71.96 | 22.2 | not measured | 0.84 | 0.74 | not measured | 1.01 | 0.62 | not measured | not measured | 119.84 | 6.95 | 35000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0299 | Not meassured | Not meassured | 13.2291 | Not meassured | Not meassured | Not meassured | 0.492 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.3156 | Not meassured | Not meassured | -0.011 | Not meassured | Not meassured | Not meassured | Not meassured | 10.9446 | Not meassured | Not meassured | 0.374 | 2.347 | Not meassured | Not meassured | 147.274 | 0.05 | 14.0524 | 0.25 | 0.92274 | 0.5 | 1.5932 | 1.5737 | 0.05 | 0.20021 | 0.25 | 0.5 | 0.25 | 0.5 | 0.052553 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-06-10 | AA | DBP | SW | CL | not given | 7.05 | 71.6 | 22 | not measured | 0.55 | 0.21 | not measured | 0.02 | 0.01 | not measured | not measured | 239.68 | 3.43 | 270000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not meassured | Not meassured | Not meassured | Not meassured | 0.019 | Not meassured | Not meassured | 2.6586 | Not meassured | Not meassured | Not meassured | 0.1573 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | -0.006 | Not meassured | Not meassured | -0.011 | Not meassured | Not meassured | Not meassured | Not meassured | 12.1256 | Not meassured | Not meassured | 0.325 | 1.16 | Not meassured | Not meassured | 1.1664 | 0.05 | 1.3941 | 0.25 | 0.05 | 0.5 | 0.05 | 2.5501 | 0.05 | 0.059401 | 0.25 | 0.5 | 0.25 | 0.5 | 4.2977 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-06-10 | AA | SW | SW | CL | not given | 7.3 | 66.2 | 19 | not measured | 0 | 0 | not measured | 0 | 0 | not measured | not measured | 119.84 | 7.51 | 60000000 | 15150 | 100 | 35000 | not done | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 3226947.6918 | 25.809 | 25.5738 | 37460.9477 | 25601.9796 | 1996.7902 | 32 | 44 | 16 | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 6.3744 | Not meassured | Not meassured | Not meassured | 0.0683 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.292 | Not meassured | Not meassured | -0.011 | Not meassured | Not meassured | Not meassured | Not meassured | 12.2184 | Not meassured | Not meassured | 0.389 | 1.545 | Not meassured | Not meassured | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-18 | AA | EP | SW | CL | not given | 7.66 | 69.26 | 20.7 | 0.006 | 1.87 | 1.84 | not measured | 1.77 | 1.58 | not measured | not measured | 85.6 | 7.27 | 1070000 | 5 | 0 | 2500 | Bacillus | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.1174 | -0.004 | 0.0397 | -0.005 | 0.0861 | 36.92 | -0.0003 | 12.4251 | 0.0012 | 0.0013 | 0.0253 | 0.5451 | 1.418 | -0.005 | 6.238 | -0.001 | 6.661 | -0.001 | -0.005 | 0.2538 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 2.265 | -0.001 | 14.2183 | 0.5052 | 4.899 | 0.272 | 0.843 | -0.001 | 0.001 | 38.6482 | 0.05 | 7.3827 | 0.25 | 0.17187 | 0.5 | 0.13954 | 1.0694 | 0.05 | 0.064589 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-18 | AA | MP | SW | CL | not given | 7.7 | 72.14 | 22.3 | 0.007 | 0.24 | 0.22 | not measured | 0.27 | 0.17 | not measured | not measured | 85.6 | 7.55 | 7500 | 5 | 5 | 1500 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.053 | -0.004 | 0.0386 | -0.005 | 0.076 | 36.21 | -0.0003 | 13.4868 | 0.001 | -0.001 | 0.0104 | 0.4944 | 1.561 | -0.005 | 5.233 | -0.001 | 6.94 | -0.001 | -0.005 | 0.4071 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 2.538 | -0.001 | 13.3892 | 0.4499 | 4.468 | 0.421 | 1.102 | -0.001 | 0.0187 | 85.8439 | 0.05 | 9.3501 | 0.25 | 0.15215 | 0.5 | 0.15561 | 1.0555 | 0.05 | 0.0779 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-18 | AA | MRT | SW | CL | not given | 7.52 | 73.76 | 23.2 | 0.006 | 1.91 | 1.82 | not measured | 1.81 | 1.48 | not measured | not measured | 85.6 | 6.79 | 47500 | 703 | 5 | 1000 | 12 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0701 | -0.004 | 0.0401 | -0.005 | 0.0562 | 36.32 | -0.0003 | 12.8881 | -0.001 | 0.0016 | 0.0071 | 0.5515 | 1.417 | -0.005 | 5.908 | 0.0013 | 6.703 | -0.001 | -0.005 | 0.3008 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 2.399 | -0.001 | 13.8894 | 0.4799 | 4.808 | 0.324 | 0.9 | -0.001 | 0.0035 | 51.5808 | 0.05 | 7.517 | 0.25 | 0.19201 | 0.5 | 0.18905 | 0.95338 | 0.05 | 0.069649 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-18 | AA | TANK | SW | CL | not given | 7.67 | 65.3 | 18.5 | 0.006 | 1.03 | 1.06 | not measured | 0.98 | 0.83 | not measured | not measured | 68.48 | 6.94 | 5000 | 30 | 5 | 1000 | 2 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0727 | -0.004 | 0.0404 | -0.005 | 0.0517 | 35.75 | -0.0003 | 13.2425 | -0.001 | 0.0012 | 0.0044 | 0.516 | 1.418 | -0.005 | 5.745 | -0.001 | 7.131 | -0.001 | -0.005 | 0.4054 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 2.529 | -0.001 | 13.3118 | 0.4701 | 4.426 | 0.398 | 1.13 | -0.001 | 0.0201 | 65.1321 | 0.05 | 7.4382 | 0.25 | 0.17088 | 0.5 | 0.22934 | 0.80314 | 0.05 | 0.079919 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-18 | AA | TCR | SW | CL | not given | 7.56 | 70.88 | 21.6 | 0.007 | 0.47 | 0.4 | not measured | 0.58 | 0.44 | not measured | not measured | 85.6 | 7.19 | 5000 | 5 | 5 | 15500 | 20.5 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0641 | -0.004 | 0.0409 | -0.005 | -0.008 | 36.74 | -0.0003 | 577.99 | 0.001 | -0.001 | 0.0067 | 0.5096 | 1.475 | -0.005 | 5.337 | -0.001 | 7.137 | -0.001 | -0.005 | 0.4399 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 2.579 | -0.001 | 14.9369 | 0.4582 | 4.428 | 0.412 | 1.021 | -0.001 | 0.0032 | 93.9902 | 0.05 | 9.4986 | 0.25 | 0.15282 | 0.5 | 0.18371 | 1.0165 | 0.05 | 0.082496 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-18 | AA | DBP | SW | CL | not given | 7.43 | 62.96 | 17.2 | 0.005 | 1.02 | 0.92 | not measured | 0.98 | 0.85 | not measured | not measured | 171.2 | 3.61 | 7500 | 20 | 5 | 2500 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | -0.004 | -0.004 | 0.0506 | -0.005 | -0.008 | 56.84 | -0.0003 | 524.9588 | -0.001 | 0.007 | 0.0195 | 0.1697 | 2.215 | -0.005 | 27.1 | -0.001 | 3.801 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 4.572 | -0.001 | 100.8315 | 0.4017 | 33.85 | 0.014 | 0.248 | -0.001 | 0.0034 | 2.0176 | 0.05 | 2.2072 | 0.25 | 0.05 | 0.5 | 0.05 | 1.7714 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.41 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-18 | AA | SW | SW | CL | not given | 7.63 | 69.44 | 20.8 | 0 | 0 | 0 | not measured | 0 | 0 | not measured | not measured | 102.72 | 7.36 | 8500000 | 0 | 50 | 10000 | 1 | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 290671.6755 | 30.1003 | 26.4938 | 4246 | 20387.4885 | 3838.8774 | 32 | 44 | 16 | 0.0248 | -0.004 | 0.041 | -0.005 | -0.008 | 37.57 | -0.0003 | 7.3114 | -0.001 | 0.0075 | 0.0584 | 0.1349 | 1.522 | -0.005 | 7.021 | 0.0106 | 5.428 | -0.001 | -0.005 | 0.2565 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 2.55 | -0.001 | 13.7099 | 0.5069 | 4.565 | 0.334 | 1.261 | -0.001 | 0.0031 | 2.0908 | 0.05 | 0.26942 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-22 | AA | EP | SW | CL | not given | 7.38 | 39.38 | 4.1 | 0.006 | 2.56 | 2.39 | not measured | 2.23 | 1.67 | not measured | not measured | 188.32 | 7.75 | 5000 | 0 | 0 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0887 | -0.004 | 0.0213 | -0.005 | -0.008 | 49.63 | -0.0003 | 15.5137 | 0.0011 | -0.001 | 0.0065 | 0.7036 | 1.262 | -0.005 | 12.93 | 0.0017 | 6.215 | -0.001 | -0.005 | 0.6315 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 0.8937 | -0.001 | 9999999999999990 | 0.0898 | 2.425 | 0.627 | 0.861 | -0.001 | 0.0018 | 33.3712 | 0.05 | 4.2152 | 0.25 | 0.10263 | 0.5 | 0.088724 | 0.42431 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-22 | AA | MP | SW | CL | not given | 7.51 | 48.74 | 9.3 | 0.006 | 2.14 | 2.04 | not measured | 1.94 | 1.62 | not measured | not measured | 171.2 | 7.28 | 30000 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 127.7632 | 38.8793 | 38.1722 | 44 | 22 | 8 | 32 | 44 | 16 | 0.0562 | -0.004 | 0.0202 | -0.005 | -0.008 | 51.51 | -0.0003 | 16.8126 | -0.001 | 0.0019 | 0.0031 | 0.7253 | 1.531 | -0.005 | 12.13 | -0.001 | 6.532 | -0.001 | -0.005 | 0.6109 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 1.254 | -0.001 | 9999999999999990 | 0.0946 | 2.56 | 0.613 | 1.001 | -0.001 | 0.0008 | 56.7137 | 0.05 | 4.9995 | 0.25 | 0.11373 | 0.5 | 0.20487 | 0.39394 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-22 | AA | MRT | SW | CL | not given | 7.55 | 48.74 | 9.3 | 0.006 | 0.93 | 0.77 | not measured | 0.71 | 0.56 | not measured | not measured | 188.32 | 7.22 | 5000 | 5 | 5 | 1000 | 1.5 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 171.039 | 38.0012 | 37.414 | 44 | 7138.9702 | 8 | 32 | 44 | 16 | 0.0507 | -0.004 | 0.0224 | -0.005 | -0.008 | 47.36 | -0.0003 | 16.961 | -0.001 | 0.0023 | 0.0017 | 0.7193 | 2.028 | -0.005 | 13.63 | -0.001 | 6.171 | -0.001 | -0.005 | 0.3797 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 1.861 | -0.001 | 9999999999999990 | 0.0827 | 2.367 | 0.39 | 1.236 | -0.001 | 0.0024 | 64.4441 | 0.05 | 4.3317 | 0.25 | 0.15861 | 0.5 | 0.15085 | 0.31102 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-22 | AA | TANK | SW | CL | not given | 7.58 | 46.4 | 8 | 0.007 | 2.15 | 1.33 | not measured | 1.07 | 0.9 | not measured | not measured | 188.32 | 7.42 | 2395000 | 5 | 5 | 6000 | Bacillus | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0755 | -0.004 | 0.0229 | -0.005 | -0.008 | 49.87 | -0.0003 | 17.1006 | -0.001 | 0.0283 | 0.0147 | 0.7223 | 1.891 | 0.0062 | 12.71 | 0.0026 | 6.436 | -0.001 | -0.005 | 0.5129 | Not meassured | 0.0032 | -0.011 | 0.0074 | -0.003 | 1.646 | -0.001 | 9999999999999990 | 0.0918 | 2.571 | 0.52 | 1.271 | -0.001 | 0.009 | 86.8424 | 0.05 | 5.5872 | 0.25 | 0.25196 | 0.5 | 0.17209 | 0.33717 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-22 | AA | TCR | SW | CL | not given | 7.35 | 48.92 | 9.4 | 0.007 | 2.24 | 2.16 | not measured | 1.94 | 1.7 | not measured | not measured | 188.32 | 7.39 | 80000 | 5 | 5 | 1000 | 2 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0591 | -0.004 | 0.022 | -0.005 | -0.008 | 51.56 | -0.0003 | 16.7658 | -0.001 | 0.0025 | 0.0021 | 0.7239 | 1.477 | 0.0074 | 12.55 | -0.001 | 6.566 | -0.001 | -0.005 | 0.6173 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 1.274 | -0.001 | 9999999999999990 | 0.0973 | 2.698 | 0.621 | 1.097 | -0.001 | 0.0013 | 46.665 | 0.05 | 4.2014 | 0.25 | 0.085799 | 0.5 | 0.11196 | 0.32788 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-22 | AA | DBP | SW | CL | not given | 7.5 | 48.92 | 9.4 | 0.006 | 0.88 | 0.78 | not measured | 0.75 | 0.55 | not measured | not measured | 188.32 | 7.32 | 5000 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0502 | -0.004 | 0.0231 | -0.005 | -0.008 | 48.17 | -0.0003 | 16.9444 | -0.001 | 0.0029 | -0.001 | 0.7216 | 2.109 | 0.0142 | 13.74 | -0.001 | 6.102 | -0.001 | -0.005 | 0.3882 | Not meassured | -0.002 | -0.011 | -0.005 | 0.0037 | 1.822 | -0.001 | 9999999999999990 | 0.0836 | 2.343 | 0.4 | 1.295 | -0.001 | 0.0022 | 83.1956 | 0.05 | 5.5985 | 0.25 | 0.18503 | 0.5 | 0.20366 | 0.39395 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-22 | AA | SW | SW | CL | not given | 7.82 | 38.12 | 3.4 | not measured | 0 | 0 | not measured | 0 | 0 | not measured | not measured | 188.32 | 7.85 | 6000000 | 410 | 50 | 10000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 1005763.0107 | 25.9503 | 26.5391 | 4246 | 9995.478 | 6998.3688 | 32 | 44 | 16 | 0.0147 | -0.004 | 0.0245 | -0.005 | -0.008 | 49.88 | -0.0003 | 7.6764 | -0.001 | -0.001 | 0.0272 | 0.0673 | 1.478 | 0.0105 | 13.69 | 0.0579 | 4.55 | -0.001 | 0.0207 | 0.631 | Not meassured | -0.002 | -0.011 | 0.0057 | -0.003 | 0.7381 | -0.001 | 9999999999999990 | 0.0944 | 2.283 | 0.663 | 1.211 | -0.001 | 0.0023 | 0.07726 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | BP | EP | SW | CLM | 12 | 8.42 | 42.6 | 5.8889 | 0.007 | 3 | not measured | 0.06 | 2.58 | not measured | 2.5 | 0 | 68.48 | 9.31 | 7500 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 9217.6798 | 30.8881 | 31.4567 | 280.552 | 374.7006 | 137.9191 | 32 | 44 | 16 | 0.018 | -0.004 | 0.0197 | -0.005 | -0.008 | 9.772 | -0.0003 | 17.8449 | -0.001 | 0.0124 | 0.0068 | 0.6166 | 1.642 | -0.005 | 3.978 | -0.001 | 14.74 | -0.001 | -0.005 | 0.8953 | Not meassured | -0.002 | 0.6046 | 0.489 | -0.003 | 3.57 | -0.001 | 7.8406 | 0.0452 | 3.088 | 1.101 | 1.147 | -0.001 | 0.1045 | 25.0981 | 0.05 | 3.4999 | 0.25 | 0.62521 | 0.5 | 0.35372 | 0.28095 | 0.05 | 0.11491 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | BP | MP | SW | CLM | 18 | 8.25 | 47.8 | 8.7778 | 0.008 | 2.7 | not measured | 0.04 | 1.85 | not measured | 1.48 | 0.08 | 68.48 | 9.34 | 5000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 25757.9298 | 30.6432 | 30.9693 | 752.9513 | 718.8661 | 155.8697 | 32 | 44 | 16 | 0.0167 | -0.004 | 0.0198 | -0.005 | -0.008 | 9.164 | -0.0003 | 17.8356 | -0.001 | 0.0012 | 0.0026 | 0.6279 | 1.583 | -0.005 | 3.635 | 0.001 | 13.86 | -0.001 | -0.005 | 0.8749 | Not meassured | -0.002 | 0.551 | 0.5145 | -0.003 | 3.588 | -0.001 | 7.6741 | 0.043 | 2.676 | 1.079 | 1.03 | -0.001 | 0.1097 | 23.7979 | 0.05 | 3.7938 | 0.25 | 0.47876 | 0.5 | 0.33637 | 0.36104 | 0.05 | 0.081021 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | BP | MRT | SW | CLM | 24 | 8.19 | 45.8 | 7.6667 | 0.009 | 0.6 | not measured | 0.05 | 0.43 | not measured | 0.2 | 0.21 | 51.36 | 9.4 | 50500 | 5 | 5 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 18453.3862 | 29.7902 | 29.9823 | 954.9071 | 22 | 289.7616 | 32 | 44 | 16 | 0.0248 | -0.004 | 0.0189 | -0.005 | -0.008 | 9.384 | -0.0003 | 16.4304 | -0.001 | 0.0022 | 0.0151 | 0.6059 | 1.529 | -0.005 | 3.662 | -0.001 | 12.91 | -0.001 | -0.005 | 0.8983 | Not meassured | -0.002 | 0.5652 | 0.5067 | -0.003 | 3.599 | -0.001 | 7.7413 | 0.0446 | 2.58 | 1.035 | 0.968 | -0.001 | 0.0938 | 21.2549 | 0.05 | 3.5072 | 0.25 | 0.38093 | 0.5 | 0.20978 | 0.32846 | 0.05 | 0.06081 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | BP | TANK | SW | CLM | 19 | 8.33 | 56.2 | 13.4444 | 0.008 | 3.1 | not measured | 0.1 | 2.71 | not measured | 2.6 | 0 | 51.36 | 9.1 | 55000 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 28919.6516 | 30.1138 | 30.1096 | 791.1035 | 696.2637 | 110.5513 | 32 | 44 | 16 | 0.0193 | -0.004 | 0.0198 | -0.005 | -0.008 | 9.194 | -0.0003 | 17.8031 | -0.001 | -0.001 | 0.0034 | 0.6695 | 1.626 | -0.005 | 3.622 | 0.0013 | 13.92 | -0.001 | -0.005 | 0.869 | Not meassured | -0.002 | 0.5861 | 0.5184 | -0.003 | 3.691 | -0.001 | 7.7441 | 0.0437 | 2.551 | 1.115 | 1.114 | -0.001 | 0.1129 | 27.0366 | 0.05 | 3.697 | 0.25 | 0.58825 | 0.5 | 0.42722 | 0.29863 | 0.05 | 0.1086 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | BP | TCR | SW | CLM | 20 | 8.61 | 47.1 | 8.3889 | 0.008 | 2.2 | not measured | 0.05 | 1.75 | not measured | 1.32 | 0.1 | 51.36 | 9.31 | 15000 | 5 | 5 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 8637.2707 | 27.3234 | 29.0308 | 249.8427 | 400.2413 | 28.6755 | 32 | 44 | 16 | 0.0206 | -0.004 | 0.0194 | -0.005 | -0.008 | 9.453 | -0.0003 | 17.8653 | -0.001 | 0.0053 | 0.0048 | 0.629 | 1.451 | -0.005 | 3.722 | -0.001 | 13.86 | -0.001 | -0.005 | 0.8799 | Not meassured | -0.002 | 0.5245 | 0.4983 | -0.003 | 3.715 | -0.001 | 7.6331 | 0.0451 | 2.527 | 1.067 | 0.975 | -0.001 | 0.0976 | 22.9213 | 0.05 | 3.7441 | 0.25 | 0.44859 | 0.5 | 0.28912 | 0.35681 | 0.05 | 0.070935 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | BP | DBP | SW | CLM | 18 | 7.97 | 46.4 | 8 | 0.009 | 2.2 | not measured | 0.1 | 1.87 | not measured | 1.34 | 0.1 | 51.36 | 9.32 | 37500 | 5 | 5 | 1000 | 1 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 31988.3846 | 31.7938 | 27.1244 | 735.5646 | 22 | 91.9925 | 32 | 44 | 16 | 0.0203 | -0.004 | 0.0198 | -0.005 | -0.008 | 9.494 | -0.0003 | 17.8972 | -0.001 | 0.0046 | 0.0046 | 0.6549 | 1.429 | -0.005 | 3.676 | -0.001 | 13.87 | -0.001 | -0.005 | 0.8805 | Not meassured | -0.002 | 0.5851 | 0.5002 | -0.003 | 3.721 | -0.001 | 7.6577 | 0.0446 | 2.544 | 1.039 | 0.966 | -0.001 | 0.1004 | 22.1538 | 0.05 | 3.6355 | 0.25 | 0.47353 | 0.5 | 0.31929 | 0.35145 | 0.05 | 0.07311 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-02-04 | BP | SW | SW | CLM | 2 | 8.8 | 42 | 5.5556 | 0.012 |  | not measured |  | 0 | not measured | 0 | 0.05 | 68.48 | 9.09 | 3050000 | 72800 | 520 | 10000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 11970015.4166 | 2039 | 1416 | 2551894.3374 | 25.2714 | 27.3379 | 177345.4818 | 126477.7806 | 13760.6886 | 32 | 44 | 16 | 0.0781 | -0.004 | 0.0214 | -0.005 | -0.008 | 9.383 | -0.0003 | 9.0258 | -0.001 | 0.0016 | 0.1418 | 0.0782 | 1.554 | -0.005 | 3.822 | 0.0153 | 5.781 | -0.001 | -0.005 | 0.9153 | Not meassured | -0.002 | -0.011 | 0.0138 | -0.003 | 4.175 | -0.001 | 5.0447 | 0.0449 | 1.712 | 0.765 | 1.468 | -0.001 | 0.0037 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-05-05 | BP | EP | SW | CLM | 12 | 7.06 | 62.24 | 16.8 | 0.009 | 2.6 | not measured | 0.04 | 2.38 | not measured | 2.36 | 0.04 | 51.36 | 6.78 | Mold | 0 | 0 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 1710.2983 | 31.4398 | 31.2051 | 40 | 2814.5809 | 8 | 32 | 44 | 16 | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 17.4802 | Not meassured | Not meassured | Not meassured | 0.6538 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.5015 | Not meassured | Not meassured | 0.4057 | Not meassured | Not meassured | Not meassured | Not meassured | 8.3648 | Not meassured | Not meassured | 1 | 1.14 | Not measured | Not measured | 65.8227 | 0.05 | 10.8163 | 0.25 | 1.7427 | 0.5 | 2.7814 | 0.9538 | 0.05 | 0.74838 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-05-05 | BP | MP | SW | CLM | 18 | 7.41 | 63.14 | 17.3 | 0.012 | 1.3 | not measured | 0.02 | 0.79 | not measured | 0.73 | 0.18 | 68.48 | 7.27 | Mold | 5 | 5 | 1000 | 5 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 2447.3342 | 31.1881 | 30.6824 | 40 | 22 | 2762.2856 | 32 | 44 | 16 | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 18.3615 | Not meassured | Not meassured | Not meassured | 0.6456 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.531 | Not meassured | Not meassured | 0.4204 | Not meassured | Not meassured | Not meassured | Not meassured | 8.3564 | Not meassured | Not meassured | 0.969 | 1.196 | Not measured | Not measured | 59.4801 | 0.05 | 10.264 | 0.25 | 1.8835 | 0.5 | 1.6682 | 0.98222 | 0.05 | 0.48111 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-05-05 | BP | MRT | SW | CLM | 24 | 7.28 | 61.34 | 16.3 | 0.021 | 0.5 | not measured | 0.02 | 0.37 | not measured | 0.31 | 0.19 | 68.48 | 7.41 | 12500 | 5 | 5 | 1000 | 2 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 12147.168 | 28.3752 | 28.2163 | 1028.5877 | 60470.0913 | 11999.0164 | 32 | 44 | 16 | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 18.6063 | Not meassured | Not meassured | Not meassured | 0.6454 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0215 | 0.5701 | Not meassured | Not meassured | 0.4359 | Not meassured | Not meassured | Not meassured | Not meassured | 8.4049 | Not meassured | Not meassured | 1.04 | 1.652 | Not measured | Not measured | 57.1684 | 0.05 | 10.1646 | 0.25 | 1.735 | 0.5 | 1.1952 | 0.96912 | 0.05 | 0.47322 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-05-05 | BP | TANK | SW | CLM | 19 | 7.57 | 63.14 | 17.3 | 0.01 | 1.9 | not measured | 0.03 | 1.54 | not measured | 1.46 | 0.11 | 68.48 | 7.42 | 5000 | 5 | 5 | 1000 | 6 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 4058.1691 | 30.5007 | 32.0182 | 40 | 10928.7052 | 8 | 32 | 44 | 16 | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 17.9136 | Not meassured | Not meassured | Not meassured | 0.6522 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.5174 | Not meassured | Not meassured | 0.4234 | Not meassured | Not meassured | Not meassured | Not meassured | 8.322 | Not meassured | Not meassured | 1.011 | 1.144 | Not measured | Not measured | 51.7287 | 0.05 | 9.0932 | 0.25 | 1.8425 | 0.5 | 1.8226 | 0.86314 | 0.05 | 0.51046 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-05-05 | BP | TCR | SW | CLM | 20 | 7.66 | 63.86 | 17.7 | 0.009 | 1.9 | not measured | 0.03 | 1.8 | not measured | 1.75 | 0.09 | 68.48 | 7.15 | 10000 | 5 | 5 | 1000 | 3.5 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 1797.4128 | 30.1248 | 31.9565 | 40 | 22 | 2670.6182 | 32 | 44 | 16 | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 17.8601 | Not meassured | Not meassured | Not meassured | 0.6593 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | -0.005 | 0.5183 | Not meassured | Not meassured | 0.405 | Not meassured | Not meassured | Not meassured | Not meassured | 8.3682 | Not meassured | Not meassured | 0.984 | 1.155 | Not measured | Not measured | 52.8647 | 0.05 | 9.1734 | 0.25 | 1.5423 | 0.5 | 2.0335 | 0.83348 | 0.05 | 0.54293 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2026-05-05 | BP | DBP | SW | CLM | 18 | 7.66 | 63.86 | 17.7 | 0.007 | 1.2 | not measured | 0.03 | 0.89 | not measured | 0.82 | 0.17 | 85.6 | 7.26 | 75000 | 5 | 5 | 1000 | 8 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 181352.4729 | 28.6073 | 31.1886 | 40 | 22 | 1507.1096 | 32 | 44 | 16 | Not meassured | Not meassured | Not meassured | Not meassured | -0.008 | Not meassured | Not meassured | 18.384 | Not meassured | Not meassured | Not meassured | 0.6448 | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | Not meassured | 0.0194 | 0.5314 | Not meassured | Not meassured | 0.4238 | Not meassured | Not meassured | Not meassured | Not meassured | 8.3724 | Not meassured | Not meassured | 0.953 | 1.21 | Not measured | Not measured | 57.6098 | 0.05 | 10.4903 | 0.25 | 1.6311 | 0.5 | 1.5023 | 0.99696 | 0.05 | 0.48386 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-09 | BP | EP | SW | CLM | 12 | 7.62 | 69.8 | 21 | 0.009 | 2.4 | not measured | 0.13 | 1.82 | not measured | 1.8 | 0.15 | 68.48 | 5.54 | 45000 | 0 | 0 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 40.161 | 33.1657 | 32.9845 | 40 | 22 | 8 | 32 | 44 | 16 | 0.097 | -0.004 | 0.0201 | -0.005 | -0.008 | 10.71 | -0.0003 | 13.4466 | -0.001 | 0.0032 | 0.003 | 0.6253 | 2.019 | -0.005 | 4.313 | -0.001 | 11.1 | -0.001 | 0.0991 | 0.4219 | Not meassured | -0.002 | 0.3542 | 0.3991 | -0.003 | 3.051 | -0.001 | 7.4233 | 0.0527 | 2.493 | 0.943 | 1.44 | -0.001 | 0.0654 | 22.1294 | 0.05 | 3.9123 | 0.93189 | 0.27073 | 0.5 | 0.23075 | 0.38119 | 0.05 | 0.20773 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-09 | BP | MP | SW | CLM | 18 | 7.61 | 72.5 | 22.5 | 0.232 | 0.4 | not measured | 0.06 | 0.14 | not measured | 0.08 | 0.07 | 85.6 | 5.45 | 160000 | 5 | 5 | 1000 | Bacillus | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 3406.9451 | 28.6586 | 32.2364 | 40 | 580.8224 | 8 | 32 | 44 | 16 | 0.0706 | -0.004 | 0.0199 | -0.005 | -0.008 | 11.03 | -0.0003 | 14.1671 | -0.001 | 0.0054 | 0.0047 | 0.5867 | 1.966 | 0.006 | 4.401 | -0.001 | 11.11 | -0.001 | 0.2992 | 0.6374 | Not meassured | -0.002 | 0.4312 | 0.4029 | -0.003 | 3.012 | -0.001 | 7.4494 | 0.0534 | 2.49 | 1 | 1.328 | -0.001 | 0.0673 | 19.7321 | 0.05 | 3.2232 | 2.2387 | 0.19738 | 0.5 | 0.14752 | 0.28839 | 0.05 | 0.16282 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-09 | BP | MRT | SW | CLM | 24 | 7.82 | 73.58 | 23.1 | 0.262 | 0.1 | not measured | 0 | 0.03 | not measured | 0 | 0.04 | 68.48 | 5.72 | 845000 | 5 | 5 | 1000 | 76 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 7245.1376 | 27.7794 | 27.3383 | 40 | 304.2029 | 8 | 32 | 44 | 16 | 0.06 | -0.004 | 0.0208 | -0.005 | -0.008 | 11.32 | -0.0003 | 14.3393 | -0.001 | 0.0136 | 0.0068 | 0.5821 | 1.923 | -0.005 | 4.602 | 0.0012 | 11.8 | -0.001 | 0.3159 | 0.6252 | Not meassured | -0.002 | 0.3489 | 0.3844 | -0.003 | 3.031 | -0.001 | 7.6252 | 0.0564 | 2.586 | 0.999 | 1.291 | -0.001 | 0.0663 | 3.3031 | 0.05 | 0.77177 | 4.8141 | 0.14596 | 0.5 | 0.05 | 0.10416 | 0.05 | 0.05481 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-09 | BP | TANK | SW | CLM | 19 | 7.74 | 73.58 | 23.1 | 0.255 | 0.3 | not measured | 0 | 0.03 | not measured | 0.01 | 0.02 | 68.48 | 5.92 | 30000 | 5 | 5 | 1000 | 206 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 7366.1631 | 28.0676 | 28.0098 | 40 | 22 | 8 | 32 | 44 | 16 | 0.0883 | -0.004 | 0.021 | -0.005 | -0.008 | 11.22 | -0.0003 | 14.3447 | -0.001 | -0.001 | 0.0051 | 0.5931 | 1.856 | -0.005 | 4.59 | -0.001 | 11.78 | -0.001 | 0.3237 | 0.6236 | Not meassured | -0.002 | 0.3712 | 0.3932 | -0.003 | 3.037 | -0.001 | 7.5773 | 0.0556 | 2.56 | 1.004 | 1.323 | -0.001 | 0.063 | 20.326 | 0.05 | 3.2895 | 5.7681 | 0.16546 | 0.5 | 0.05 | 0.29154 | 0.05 | 0.17005 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-09 | BP | TCR | SW | CLM | 20 | 7.57 | 71.24 | 21.8 | 0.25 | 0.5 | not measured | 0.03 | 0.11 | not measured | 0.04 | 0 | 68.48 | 6.09 | 205000 | 5 | 5 | 1000 | 134 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 4015.7714 | 28.4005 | 28.2886 | 40 | 22 | 58.2083 | 32 | 44 | 16 | 0.0736 | -0.004 | 0.0205 | -0.005 | -0.008 | 11.1 | -0.0003 | 14.1855 | -0.001 | 0.002 | 0.0073 | 0.5789 | 1.846 | -0.005 | 4.533 | 0.002 | 11.46 | -0.001 | 0.2971 | 0.6425 | Not meassured | -0.002 | 0.3793 | 0.4061 | -0.003 | 3.008 | -0.001 | 7.574 | 0.055 | 2.534 | 1.005 | 1.357 | -0.001 | 0.0696 | 19.36 | 0.05 | 3.1745 | 2.4045 | 0.18612 | 0.5 | 0.12455 | 0.27854 | 0.05 | 0.15541 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-09 | BP | DBP | SW | CLM | 18 | 7.72 | 72.5 | 22.5 | 0.269 | 0.2 | not measured | 0 | 0.06 | not measured | 0.02 | 0.01 | 68.48 | 5.99 | 200000 | 5 | 5 | 1000 | 355 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 3606.2277 | 28.5622 | 28.5103 | 40 | 281.8259 | 19.728 | 32 | 44 | 16 | 0.0771 | -0.004 | 0.0208 | -0.005 | -0.008 | 11.26 | -0.0003 | 14.228 | -0.001 | 0.01 | 0.0058 | 0.5834 | 1.882 | -0.005 | 4.607 | 0.001 | 11.7 | -0.001 | 0.3304 | 0.6638 | Not meassured | -0.002 | 0.4312 | 0.4013 | -0.003 | 3.006 | -0.001 | 7.477 | 0.056 | 2.572 | 0.968 | 1.299 | -0.001 | 0.0691 | 20.5286 | 0.05 | 3.2713 | 2.5166 | 0.17627 | 0.5 | 0.10982 | 0.29265 | 0.05 | 0.16212 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-09-09 | BP | SW | SW | CLM | 2 | 7.66 | 73.4 | 23 | 0 | 0 | not measured | 0 | 0.03 | not measured | 0.01 | 0.08 | 68.48 | 7.15 | 38000000 | 14800 | 500 | 100000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 232272.0959 | 28.9811 | 29.9733 | 4246 | 434 | 1935.2879 | 32 | 44 | 16 | -0.004 | -0.004 | 0.0228 | -0.005 | -0.008 | 10.56 | -0.0003 | 6.5585 | -0.001 | 0.0019 | 0.0593 | 0.0931 | 1.984 | -0.005 | 4.58 | 0.0203 | 4.729 | -0.001 | 0.1037 | 0.3859 | Not meassured | -0.002 | -0.011 | 0.0187 | -0.003 | 3.284 | -0.001 | 4.5197 | 0.0545 | 1.548 | 0.493 | 1.756 | 0.0011 | 0.0034 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-17 | BP | EP | SW | CLM | 12 | 8.41 | 46.58 | 8.1 | 0.012 | 3 | not measured | 0.05 | 2.6 | not measured | 2.65 | 0.01 | 68.48 | 7.6 | 7500 | 0 | 0 | 1000 | 4 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 4856.6789 | 32.6849 | 28.6423 | 40 | 39638.479 | 651.1227 | 32 | 44 | 16 | 0.0465 | -0.004 | 0.0197 | -0.005 | -0.008 | 11.74 | -0.0003 | 14.6381 | -0.001 | -0.001 | 0.0064 | 0.5877 | 2.017 | -0.005 | 4.818 | 0.0025 | 12.2 | -0.001 | 0.0146 | 0.4794 | Not meassured | -0.002 | 0.4005 | 0.4584 | -0.003 | 2.615 | -0.001 | 8.0781 | 0.0683 | 2.893 | 0.977 | 1.066 | -0.001 | 0.0995 | 15.0667 | 0.05 | 3.2586 | 0.25 | 0.19287 | 0.5 | 0.42089 | 0.36238 | 0.05 | 0.24505 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-17 | BP | MP | SW | CLM | 18 | 8.04 | 48.92 | 9.4 | 0.01 | 1.5 | not measured | 0.03 | 1.22 | not measured | 0.95 | 0.14 | 68.48 | 7.4 | 150000 | 5 | 5 | 1000 | 12 | negative | Not tested | no result | no result | no result | 84 | 3554.2584 | 20.4 | 14 | 7174.7916 | 30.3585 | 32.8161 | 40 |  | 8 | 32 | 44 | 16 | 0.0491 | -0.004 | 0.0191 | -0.005 | -0.008 | 11.93 | -0.0003 | 15.6034 | -0.001 | 0.0046 | 0.0081 | 0.5859 | 1.914 | -0.005 | 4.824 | -0.001 | 12.47 | -0.001 | 0.0133 | 0.5113 | Not meassured | -0.002 | 0.456 | 0.4875 | -0.003 | 2.634 | -0.001 | 8.0585 | 0.0683 | 2.897 | 0.892 | 1.04 | -0.001 | 0.0952 | 14.9155 | 0.05 | 3.4187 | 0.25 | 0.15042 | 0.5 | 0.28233 | 0.4101 | 0.05 | 0.14206 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-17 | BP | MRT | SW | CLM | 24 | 8.71 | 51.08 | 10.6 | 0.181 | 0.4 | not measured | 0 | 0.18 | not measured | 0.05 | 0.14 | 68.48 | 7.64 | 845000 | 5 | 5 | 1000 | 22 | negative | Not tested | no result | no result | no result | 84 | 289433.2791 | 20.4 | 14 | 157285.2192 | 26.0315 | 25.1495 | 33783.4455 |  | 8 | 32 | 44 | 16 | 0.047 | -0.004 | 0.02 | -0.005 | -0.008 | 12.12 | -0.0003 | 15.9595 | -0.001 | 0.0069 | 0.0076 | 0.5806 | 1.792 | -0.005 | 4.877 | 0.0012 | 12.21 | -0.001 | 0.2676 | 0.5866 | Not meassured | -0.002 | 0.4747 | 0.48 | -0.003 | 2.525 | -0.001 | 8.0654 | 0.0709 | 2.841 | 0.959 | 1.013 | -0.001 | 0.0796 | 9.3184 | 0.05 | 2.1517 | 0.25 | 0.14733 | 0.5 | 0.070147 | 0.2423 | 0.05 | 0.10558 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-17 | BP | TANK | SW | CLM | 19 | 8.13 | 46.76 | 8.2 | 0.011 | 2.3 | not measured | 0 | 1.83 | not measured | 1.72 | 0.08 | 68.48 | 7.91 | 5000 | 5 | 5 | 1000 | 1.5 | negative | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 8285.4053 | 29.9418 | 29.8161 | 40 | 17474.4107 | 8 | 32 | 44 | 16 | 0.0576 | -0.004 | 0.0206 | -0.005 | -0.008 | 11.4 | -0.0003 | 14.917 | 0.0017 | -0.001 | 0.0357 | 0.5884 | 1.741 | -0.005 | 4.718 | 0.0013 | 12.33 | -0.001 | 0.0158 | 0.4907 | Not meassured | -0.002 | 0.4364 | 0.4721 | -0.003 | 2.587 | -0.001 | 8.0361 | 0.0677 | 2.838 | 0.928 | 1.104 | -0.001 | 0.0802 | 13.2654 | 0.05 | 3.0262 | 0.25 | 0.18928 | 0.5 | 0.35091 | 0.34451 | 0.05 | 0.15353 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-17 | BP | TCR | SW | CLM | 20 | 8.27 | 55.04 | 12.8 | 0.05 | 0.6 | not measured | 0 | 0.78 | not measured | 0.46 | 0.15 | 68.48 | 7.92 | 50000 | 5 | 5 | 1000 | 3.5 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 6037.5264 | 27.9953 | 28.2074 | 1347.3665 |  | 2652.5394 | 32 | 44 | 16 | 0.0566 | -0.004 | 0.019 | -0.005 | -0.008 | 11.57 | -0.0003 | 15.8035 | -0.001 | -0.001 | 0.0148 | 0.5936 | 1.855 | -0.005 | 4.682 | 0.0016 | 12.37 | -0.001 | 0.0608 | 0.6374 | Not meassured | -0.002 | 0.4676 | 0.4734 | -0.003 | 2.559 | -0.001 | 8.0976 | 0.0678 | 2.819 | 0.966 | 1.057 | -0.001 | 0.0696 | 14.2582 | 0.05 | 3.3309 | 0.25 | 0.18211 | 0.5 | 0.20759 | 0.38645 | 0.05 | 0.17908 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-17 | BP | DBP | SW | CLM | 18 | 8.37 | 49.64 | 9.8 | 0.01 | 2.3 | not measured | 0 | 2.27 | not measured | 2.18 | 0.04 | 68.48 | 7.99 | 12500 | 5 | 5 | 1000 | 1 | positive | Not tested | no result | no result | no result | 84 | 80 | 20.4 | 14 | 3854 | 29.6354 | 29.4588 | 40 | 6759.5737 | 870.8964 | 32 | 44 | 16 | 0.0433 | -0.004 | 0.0193 | -0.005 | -0.008 | 11.26 | 0.0013 | 14.6598 | 0.0011 | 0.0036 | 0.0248 | 0.5823 | 1.905 | -0.005 | 4.657 | 0.0025 | 11.96 | 0.0013 | -0.005 | 0.4829 | Not meassured | -0.002 | 0.3763 | 0.4675 | -0.003 | 2.562 | -0.001 | 7.9754 | 0.0663 | 2.797 | 0.956 | 1.051 | 0.0013 | 0.0837 | 12.3951 | 0.05 | 2.866 | 0.25 | 0.15304 | 0.5 | 0.40128 | 0.33494 | 0.05 | 0.19991 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2025-12-17 | BP | SW | SW | CLM | 2 | 7.95 | 46.04 | 7.8 | 0.009 | 0 | not measured | 0 | 0 | not measured | 0 | 0 | 85.6 | 8 | 5050000 | 520 | 50 | 10000 | Bacillus | positive | Not tested | no result | no result | no result | 8421 | 23346.5 | 2039 | 1416 | 4008 | 33.4185 | 30.619 | 4246 | 434 | 75 | 32 | 44 | 16 | 0.0269 | -0.004 | 0.0234 | -0.005 | -0.008 | 11.88 | -0.0003 | 7.9026 | -0.001 | 0.0021 | 0.0636 | 0.0689 | 1.95 | -0.005 | 4.978 | 0.0112 | 5.122 | -0.001 | -0.005 | 0.4631 | Not meassured | -0.002 | -0.011 | 0.0081 | -0.003 | 2.857 | -0.001 | 5.3899 | 0.0698 | 1.947 | 0.555 | 1.387 | -0.001 | 0.0028 | 0.025 | 0.05 | 0.025 | 0.25 | 0.05 | 0.5 | 0.05 | 0.025 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured | not measured
2023-01-25 | MR | EP | GW | CL | 0 | 7.43 | 52 | 11.1111 | not measured | 1.41 | 1.33 | not measured | 1.07 | 0.99 | not measured | not measured | 256.8 | 8.71 | 7500 | 5 | 5 | 1000 | 3 | negative | 5000 | No L colonies | Negative | Negative | 14.17 | 2.06 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0162 | 0.004 | 0.0211 | -0.005 | -0.008 | 58.51 | -0.0003 | 34.275 | 0.0015 | 0.0103 | 0.0033 | 1.231 | 7.354 | -0.005 | 20.31 | -0.001 | 15.16 | -0.001 | -0.005 | 6.457 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.757 | -0.001 | 39.2625 | 0.1745 | 11.83 | Not meassured | 0.681 | -0.001 | 0.0038 | 1.5067 | 0.05 | 2.071 | 0.25 | 0.05 | 0.5 | 0.05 | 2.3375 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.70508 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-01-25 | MR | MP | GW | CL | 0.83 | 7.52 | 48.2 | 9 | not measured | 1.25 | 1.16 | not measured | 1.18 | 1.04 | not measured | not measured | 256.8 | 9.36 | 5000 | 5 | 5 | 1000 | 1 | negative | 7500 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0219 | -0.005 | -0.008 | 60.32 | -0.0003 | 34.767 | 0.0012 | -0.001 | 0.0149 | 0.588 | 3.75 | -0.005 | 20.66 | 0.001 | 15.24 | -0.001 | -0.005 | 6.517 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.85 | -0.001 | 39.097 | 0.1832 | 11.97 | Not meassured | 0.388 | -0.001 | 0.0022 | 1.6906 | 0.05 | 2.0169 | 0.25 | 0.05 | 0.5 | 0.05 | 2.1246 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.64435 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-01-25 | MR | MRT | GW | CL | 1.55 | 7.51 | 46.7 | 8.1667 | not measured | 0.92 | 0.88 | not measured | 0.91 | 0.79 | not measured | not measured | 256.8 | 9.3 | 5000 | 5 | 5 | 1000 | 5 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0085 | 0.004 | 0.0236 | -0.005 | -0.008 | 61.51 | -0.0003 | 34.0415 | 0.0015 | -0.001 | 0.026 | 0.5845 | 3.151 | -0.005 | 20.97 | -0.001 | 15.52 | 0.0011 | -0.005 | 6.4605 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.912 | -0.001 | 39.2605 | 0.1876 | 11.98 | Not meassured | 0.469 | -0.001 | 0.0019 | 1.8534 | 0.05 | 2.1766 | 0.25 | 0.05 | 0.5 | 0.05 | 2.2625 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.69433 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-01-25 | MR | TANK | GW | CL | 0.015 | 7.47 | 48.1 | 8.9444 | not measured | 1.26 | 1.13 | not measured | 1.1 | 1.03 | not measured | not measured | 308.16 | 8.79 | 7500 | 5 | 5 | 1000 | 1 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0217 | -0.005 | -0.008 | 59.59 | -0.0003 | 34.16 | 0.0013 | -0.001 | 0.0037 | 0.547 | 2.916 | -0.005 | 21.02 | -0.001 | 15.8 | -0.001 | -0.005 | 6.479 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.863 | -0.001 | 39.0395 | 0.1821 | 12.27 | Not meassured | 0.515 | -0.001 | 0.0186 | 1.1298 | 0.05 | 1.7278 | 0.25 | 0.05 | 0.5 | 0.05 | 2.0471 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.63227 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-01-25 | MR | TCR | GW | CL | 0.236 | 7.5 | 50.7 | 10.3889 | not measured | 1.27 | 1.22 | not measured | 1.11 | 1.01 | not measured | not measured | 308.16 | 9.19 | 5000 | 5 | 5 | 1000 | 1 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0218 | -0.005 | -0.008 | 60.7 | -0.0003 | 34.4745 | 0.0011 | -0.001 | 0.0016 | 0.6675 | 2.838 | -0.005 | 21.28 | -0.001 | 15.49 | -0.001 | -0.005 | 6.5095 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.921 | -0.001 | 39.4135 | 0.1824 | 12.35 | Not meassured | 0.513 | -0.001 | 0.0019 | 1.4079 | 0.05 | 1.926 | 0.25 | 0.05 | 0.5 | 0.05 | 2.1556 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.66075 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-01-25 | MR | DBP | GW | CL | 0.419 | 7.5 | 49.1 | 9.5 | not measured | 1.23 | 1.17 | not measured | 1.09 | 1 | not measured | not measured | 308.16 | 9.22 | 5000 | 5 | 5 | 1000 | 1 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0223 | -0.005 | -0.008 | 60.84 | -0.0003 | 34.0745 | 0.0017 | -0.001 | 0.0033 | 0.558 | 2.622 | -0.005 | 21.47 | -0.001 | 15.56 | -0.001 | -0.005 | 6.49 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.912 | -0.001 | 39.165 | 0.1847 | 12.71 | Not meassured | 0.655 | -0.001 | 0.0017 | 1.3843 | 0.05 | 1.8397 | 0.25 | 0.05 | 0.5 | 0.05 | 2.052 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.63611 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-05-16 | MR | EP | GW | CL | 0 | 7.47 | 53.2 | 11.7778 | 0.005 | 1.5 | 1.4 | not measured | 1.25 | 1.15 | not measured | not measured | 308.16 | 6.87 | 15000 | 5 | 5 | 1000 | 3 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0162 | 0.004 | 0.0211 | -0.005 | -0.008 | 58.51 | -0.0003 | 33.811 | 0.0015 | 0.0103 | 0.0033 | 0.561 | 7.354 | -0.005 | 20.31 | -0.001 | 15.16 | -0.001 | -0.005 | 5.921 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.757 | -0.001 | 39.2625 | 0.1745 | 11.83 | Not meassured | 0.527 | -0.001 | 0.0038 | 1.0698 | 0.05 | 1.1595 | 0.25 | 0.05 | 0.5 | 0.05 | 1.4614 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.46969 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-05-16 | MR | MP | GW | CL | 0.83 | 7.44 | 60.6 | 15.8889 | 0.009 | 1.3 | 1.22 | not measured | 0.97 | 0.91 | not measured | not measured | 325.28 | 6.94 | 5000 | 5 | 5 | 1000 | 2 | negative | 12500 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0219 | -0.005 | -0.008 | 60.32 | -0.0003 | 33.6395 | 0.0012 | -0.001 | 0.0149 | 0.547 | 3.75 | -0.005 | 20.66 | 0.001 | 15.24 | -0.001 | -0.005 | 5.92 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.85 | -0.001 | 39.097 | 0.1832 | 11.97 | Not meassured | 0.42 | -0.001 | 0.0022 | 2.5963 | 0.05 | 2.0822 | 0.25 | 0.05 | 0.5 | 0.05 | 2.0126 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.59395 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-05-17 | MR | MRT | GW | CL | 1.55 | 7.63 | 64.8 | 18.2222 | 0.008 | 0.84 | 0.7 | not measured | 0.75 | 0.66 | not measured | not measured | 308.16 | 6.65 | 17500 | 5 | 5 | 1000 | Bacillus | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0085 | 0.004 | 0.0236 | -0.005 | -0.008 | 61.51 | -0.0003 | 33.856 | 0.0015 | -0.001 | 0.026 | 0.593 | 3.151 | -0.005 | 20.97 | -0.001 | 15.52 | 0.0011 | -0.005 | 5.897 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.912 | -0.001 | 39.2605 | 0.1876 | 11.98 | Not meassured | 0.401 | -0.001 | 0.0019 | 3.7934 | 0.05 | 3.2195 | 0.25 | 0.05 | 0.5 | 0.05 | 2.7731 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.77864 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-05-18 | MR | TANK | GW | CL | 0.015 | 7.64 | 52.1 | 11.1667 | 0.005 | 1.06 | 0.92 | not measured | 0.91 | 0.87 | not measured | not measured | 308.16 | 6.83 | 5000 | 5 | 5 | 1000 | 2 | positive | 7500 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0217 | -0.005 | -0.008 | 59.59 | -0.0003 | 33.2615 | 0.0013 | -0.001 | 0.0037 | 0.541 | 2.916 | -0.005 | 21.02 | -0.001 | 15.8 | -0.001 | -0.005 | 5.917 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.863 | -0.001 | 39.0395 | 0.1821 | 12.27 | Not meassured | 0.384 | -0.001 | 0.0186 | 0.98789 | 0.05 | 1.1533 | 0.25 | 0.05 | 0.5 | 0.05 | 1.5904 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.58858 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-05-19 | MR | TCR | GW | CL | 0.236 | 7.57 | 55.1 | 12.8333 | 0.008 | 1.48 | 1.42 | not measured | 1.4 | 1.28 | not measured | not measured | 273.92 | 7.19 | Mold | 5 | 5 | 1000 | 5 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0218 | -0.005 | -0.008 | 60.7 | -0.0003 | 33.789 | 0.0011 | -0.001 | 0.0016 | 0.556 | 2.838 | -0.005 | 21.28 | -0.001 | 15.49 | -0.001 | -0.005 | 5.9325 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.921 | -0.001 | 39.4135 | 0.1824 | 12.35 | Not meassured | 0.418 | -0.001 | 0.0019 | 0.91252 | 0.05 | 1.2599 | 0.25 | 0.05 | 0.5 | 0.05 | 1.4673 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.48755 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-05-20 | MR | DBP | GW | CL | 0.419 | 7.53 | 56.3 | 13.5 | 0.006 | 1.5 | 1.02 | not measured | 1.37 | 1.24 | not measured | not measured | 291.04 | 6.86 | 7500 | 5 | 5 | 1000 | 12 | negative | 7500 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0223 | -0.005 | -0.008 | 60.84 | -0.0003 | 33.82 | 0.0017 | -0.001 | 0.0033 | 0.545 | 2.622 | -0.005 | 21.47 | -0.001 | 15.56 | -0.001 | -0.005 | 5.91 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 3.912 | -0.001 | 39.165 | 0.1847 | 12.71 | Not meassured | 0.433 | -0.001 | 0.0017 | 0.95517 | 0.05 | 1.3035 | 0.25 | 0.05 | 0.5 | 0.05 | 1.5718 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.48152 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-08-25 | MR | EP | GW | CL | 0 | 7.67 | 54.8 | 12.6667 | 0.007 | 1.5 | 1.42 | not measured | 1.41 | 1.22 | not measured | not measured | 308.16 | 7.41 | 5000 | 10 | 5 | 1000 | 2 | negative | 10000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0258 | -0.005 | -0.008 | 63.83 | -0.0003 | 33.4835 | 0.0013 | -0.001 | 0.002 | 0.59 | 2.653 | -0.005 | 25.41 | -0.001 | 16.8 | -0.001 | -0.005 | 6.091 | Not meassured | -0.002 | -0.011 | 0.1861 | -0.003 | 4.492 | -0.001 | 9999999999999990 | 0.1841 | 14.54 | Not meassured | 0.411 | -0.001 | 0.0036 | 1.8246 | 0.05 | 1.9714 | 0.25 | 0.05 | 0.5 | 0.05 | 2.0008 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.64469 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 1.7 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-08-25 | MR | MP | GW | CL | 0.83 | 7.58 | 65.4 | 18.5556 | not measured | 1.37 | 1.32 | not measured | 1.3 | 1.09 | not measured | not measured | 308.16 | 7.06 | 5000 | 52 | 5 | 1000 | 4 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0247 | -0.005 | -0.008 | 63.02 | -0.0003 | 33.441 | 0.0014 | -0.001 | 0.0074 | 0.5845 | 2.467 | -0.005 | 24.54 | -0.001 | 16.01 | -0.001 | -0.005 | 6.18 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 4.384 | -0.001 | Not meassured | 0.182 | 14.3 | Not meassured | 0.309 | -0.001 | 0.0012 | 2.3524 | 0.05 | 2.2334 | 0.25 | 0.05 | 0.5 | 0.05 | 2.1532 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.64779 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 1.1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-08-26 | MR | MRT | GW | CL | 1.55 | 7.73 | 76.7 | 24.8333 | 0.004 | 0.74 | 0.71 | not measured | 0.66 | 0.54 | not measured | not measured | 291.04 | 6.96 | 80000 | 52 | 5 | 1000 | 6 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0249 | -0.005 | -0.008 | 62.67 | -0.0003 | 33.583 | 0.0013 | -0.001 | 0.0419 | 0.5755 | 2.502 | -0.005 | 24.39 | -0.001 | 15.67 | -0.001 | -0.005 | 6.0695 | Not meassured | -0.002 | -0.011 | Not meassured | -0.003 | 4.341 | -0.001 | Not meassured | 0.183 | 14.21 | Not meassured | 0.298 | -0.001 | 0.0005 | 4.7582 | 0.05 | 3.6696 | 0.25 | 0.05 | 0.5 | 0.05 | 3.395 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.92424 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 1.2 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-08-27 | MR | TANK | GW | CL | 0.015 | 7.6 | 55 | 12.7778 | 0.004 | 1.5 | 1.4 | not measured | 1.27 | 1.11 | not measured | not measured | 308.16 | 6.72 | 30000 | 20 | 5 | 1000 | 1.5 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0251 | -0.005 | -0.008 | 62.24 | -0.0003 | 33.275 | 0.0012 | 0.0017 | 0.0071 | 0.5815 | 2.461 | -0.005 | 24.55 | -0.001 | 15.8 | -0.001 | -0.005 | 6.108 | Not meassured | -0.002 | -0.011 | Not meassured | -0.003 | 4.363 | -0.001 | Not meassured | 0.1782 | 14.08 | Not meassured | 0.314 | -0.001 | 0.0054 | 2.2503 | 0.05 | 2.083 | 0.25 | 0.05 | 0.5 | 0.05 | 2.2483 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.63245 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 1.3 | 1 | 1 | 0.5 | 0.5 | 1.1 | 0.5 | 1 | 2
2023-08-28 | MR | TCR | GW | CL | 0.236 | 7.25 | 62.9 | 17.1667 | not measured | 1.25 | 1.16 | not measured | 1.2 | 0.99 | not measured | not measured | 308.16 | 7.07 | 5000 | 41 | 5 | 4000 | 3 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0247 | -0.005 | -0.008 | 61.26 | -0.0003 | 33.45 | 0.0014 | 0.0137 | 0.0066 | 0.5815 | 2.43 | -0.005 | 24.24 | -0.001 | 15.68 | -0.001 | -0.005 | 6.1305 | Not meassured | -0.002 | -0.011 | Not meassured | -0.003 | 4.287 | -0.001 | Not meassured | 0.1762 | 14.02 | Not meassured | 0.344 | -0.001 | 0.0035 | 2.7028 | 0.05 | 1.9737 | 0.25 | 0.05 | 0.5 | 0.05 | 2.1479 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.6522 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 2 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-08-25 | MR | DBP | GW | CL | 0.419 | 7.4 | 57.7 | 14.2778 | not measured | 1.48 | 1.4 | not measured | 1.38 | 1.21 | not measured | not measured | 308.16 | 7.16 | 5000 | 369 | 5 | 1000 | 3.5 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0261 | -0.005 | -0.008 | 65.3 | -0.0003 | 33.4885 | 0.0015 | -0.001 | 0.0023 | 0.581 | 2.569 | -0.005 | 25.92 | -0.001 | 16.63 | -0.001 | -0.005 | 6.131 | Not meassured | -0.002 | -0.011 | Not meassured | -0.003 | 4.584 | -0.001 | Not meassured | 0.1871 | 14.68 | Not meassured | 0.334 | -0.001 | 0.0022 | 2.083 | 0.05 | 2.0259 | 0.25 | 0.05 | 0.5 | 0.05 | 2.0112 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.64369 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 1.4 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2024-10-01 | MR | EP | GW | CL | 0 | 6.82 | 53.6 | 12 | 0.006 | 1.78 | 1.85 | not measured | 1.67 | 1.61 | not measured | not measured | 308.16 | 5.38 | 5000 | 20 | 5 | 1000 | 2 | negative | 55000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0065 | 0.004 | 0.0259 | -0.005 | -0.008 | 54.65 | -0.0003 | 33.6 | 0.0022 | 0.0039 | 0.0281 | 0.0405 | 2.443 | -0.005 | 25.03 | -0.001 | 15 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | 0.0087 | -0.003 | 3.853 | -0.001 | Not meassured | 0.1585 | 14.37 | 1.141 | 2.373 | -0.001 | 0.0026 | 0.96799 | 0.05 | 1.0631 | 0.25 | 0.05 | 0.5 | 0.05 | 1.1462 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.34635 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2024-10-01 | MR | MP | GW | CL | 0.83 | 7.15 | 66.7 | 19.2778 | 0.005 | 1.32 | 1.42 | not measured | 1.21 | 1.19 | not measured | not measured | 325.28 | 5.68 | 5000 | 52 | 5 | 1000 | 2 | positive | 45000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0261 | -0.005 | -0.008 | 55.54 | -0.0003 | 33.5762 | 0.0017 | -0.001 | 0.0237 | 0.0472 | 2.499 | -0.005 | 25.09 | 0.0019 | 14.82 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | 0.0062 | -0.003 | 3.875 | -0.001 | Not meassured | 0.1362 | 14.2 | 0.818 | 1.612 | -0.001 | 0.003 | 1.5368 | 0.05 | 1.423 | 0.25 | 0.05 | 0.5 | 0.05 | 1.3759 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.42704 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2024-10-01 | MR | MRT | GW | CL | 1.55 | 7.35 | 73 | 22.7778 | 0.007 | 1.03 | 1.08 | not measured | 0.95 | 0.71 | not measured | not measured | 342.4 | 5.86 | 5000 | 52 | 5 | 1000 | Bacillus | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.026 | -0.005 | -0.008 | 59.2 | 0.0004 | 33.5 | 0.0022 | -0.001 | 0.039 | 0.0409 | 2.6 | -0.005 | 26.86 | 0.0011 | 15.82 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | 0.017 | -0.003 | 4.147 | -0.001 | Not meassured | 0.1347 | 14.32 | 0.999 | 1.751 | -0.001 | 0.0013 | 2.5269 | 0.05 | 1.9872 | 0.25 | 0.05 | 0.5 | 0.05 | 1.7844 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.53158 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1.2 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2024-10-01 | MR | TANK | GW | CL | 0.015 | 7.29 | 53.7 | 12.0556 | 0.007 | 1.85 | 1.68 | not measured | 1.67 | 1.57 | not measured | not measured | 308.16 | 6.2 | 10000 | 41 | 5 | 1000 | 10 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0254 | -0.005 | -0.008 | 58.35 | -0.0003 | 33.4 | 0.0015 | 0.0011 | 0.014 | 0.0387 | 2.538 | -0.005 | 26.63 | -0.001 | 15.57 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | 0.0072 | -0.003 | 4.1 | -0.001 | Not meassured | 0.1277 | 14.66 | 1.028 | 1.753 | -0.001 | 0.0032 | 0.91797 | 0.05 | 0.98995 | 0.25 | 0.05 | 0.5 | 0.05 | 1.0874 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.33438 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2024-10-01 | MR | TCR | GW | CL | 0.236 | 7.39 | 53.6 | 12 | 0.006 | 1.68 | 1.65 | not measured | 1.71 | 1.68 | not measured | not measured | 308.16 | 6.37 | 5000 | 41 | 5 | 1000 | 0 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0259 | -0.005 | -0.008 | 58.23 | -0.0003 | 33.61 | 0.0015 | -0.001 | 0.0026 | 0.0389 | 2.567 | -0.005 | 26.55 | -0.001 | 15.6 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | 0.0104 | -0.003 | 4.152 | -0.001 | Not meassured | 0.1289 | 14.29 | 1.025 | 1.855 | 0.0011 | 0.001 | 0.89025 | 0.05 | 0.9319 | 0.25 | 0.05 | 0.5 | 0.05 | 0.99166 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.32531 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2024-10-01 | MR | DBP | GW | CL | 0.419 | 7.29 | 55.7 | 13.1667 | 0.006 | 1.73 | 1.68 | not measured | 1.52 | 1.48 | not measured | not measured | 256.8 | 6.4 | 5000 | 402 | 5 | 1000 | 0 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0255 | -0.005 | -0.008 | 57.53 | -0.0003 | 33.5 | 0.0027 | 0.0059 | 0.01 | 0.0354 | 2.598 | -0.005 | 26.42 | -0.001 | 15.74 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | 0.1923 | 0.1954 | -0.003 | 4.078 | -0.001 | Not meassured | 0.1279 | 14.42 | 1.071 | 2.277 | -0.001 | 0.0019 | 1.6455 | 0.05 | 1.2474 | 0.25 | 0.05 | 0.5 | 0.05 | 1.1561 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.34886 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-01-31 | JG | EP | GW | CL | not given | 7.23 | 52.6 | 11.4444 | not measured | 0.47 | 0.43 | not measured | 0.44 | 0.37 | not measured | not measured | 359.52 | 7.4 | 5000 | 5 | 5 | 1000 | 3 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0154 | -0.005 | -0.008 | 64.51 | -0.0003 | 2.8765 | -0.001 | -0.001 | 0.1893 | 0.962 | 1.058 | -0.005 | 33.12 | 0.0295 | 2.703 | 0.0012 | -0.005 | 0.0385 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 6.939 | -0.001 | Not meassured | 0.0497 | 7.8 | Not meassured | 0.348 | -0.001 | 0.0186 | 0.56107 | 0.05 | 0.77291 | 0.25 | 0.05 | 0.5 | 0.05 | 0.80251 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.21807 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-01-31 | JG | MP | GW | CL | not given | 7.41 | 47.9 | 8.8333 | not measured | 0.42 | 0.39 | not measured | 0.36 | 0.26 | not measured | not measured | 376.64 | 7.81 | 5000 | 5 | 5 | 1000 | 3 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.0067 | 0.004 | 0.0156 | -0.005 | -0.008 | 64.53 | -0.0003 | 7.034 | -0.001 | 0.0037 | 0.1221 | 1.58 | 1.101 | -0.005 | 33.26 | 0.0134 | 2.884 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 6.921 | -0.001 | 45.888 | 0.0495 | 7.929 | Not meassured | 0.423 | -0.001 | 0.007 | 0.8635 | 0.05 | 0.94169 | 0.25 | 0.05 | 0.5 | 0.05 | 0.87684 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.24736 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-01-31 | JG | MRT | GW | CL | not given | 7.35 | 57.2 | 14 | not measured | 0.38 | 0.34 | not measured | 0.34 | 0.24 | not measured | not measured | 376.64 | 7.55 | 5000 | 5 | 5 | 1000 | 5 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0161 | -0.005 | -0.008 | 65.98 | -0.0003 | 10.672 | -0.001 | 0.0072 | 0.1358 | 1.652 | 0.9968 | -0.005 | 33.72 | 0.0133 | 3.683 | -0.001 | -0.005 | 0.35 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 6.955 | -0.001 | 45.62 | 0.0507 | 7.944 | Not meassured | 0.454 | -0.001 | 0.0057 | 1.2044 | 0.05 | 1.326 | 0.25 | 0.05 | 0.5 | 0.05 | 1.2002 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.32392 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-01-31 | JG | TANK | GW | CL | not given | 7.49 | 41.7 | 5.3889 | not measured | 0.4 | 0.38 | not measured | 0.37 | 0.21 | not measured | not measured | 376.64 | 8.34 | 5000 | 5 | 5 | 1000 | 3 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.016 | -0.005 | -0.008 | 64.43 | -0.0003 | 13.83 | -0.001 | 0.0023 | 0.1512 | 1.658 | 1.11 | -0.005 | 33.89 | 0.0171 | 4.48 | 0.0013 | -0.005 | 0.452 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 7.045 | -0.001 | 45.468 | 0.0509 | 7.768 | Not meassured | 0.329 | -0.001 | 0.0044 | 0.70633 | 0.05 | 0.98976 | 0.25 | 0.05 | 0.5 | 0.05 | 1.0144 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.31275 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-04-27 | JG | EP | GW | CL | not given | 7.46 | 51.6 | 10.8889 | not measured | 0.53 | 0.38 | not measured | 0.37 | 0.3 | not measured | not measured | 325.28 | 6.95 | 10000 | 5 | 5 | 1000 | 1 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0152 | -0.005 | -0.008 | 63.01 | -0.0003 | 2.5795 | -0.001 | -0.001 | 0.132 | 0.753 | 1.128 | -0.005 | 32.18 | 0.0175 | 2.643 | 0.0011 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 6.867 | -0.001 | 22.286 | 0.0486 | 7.43 | Not meassured | 0.403 | -0.001 | 0.0073 | 0.88719 | 0.05 | 1.1002 | 0.25 | 0.05 | 0.5 | 0.05 | 1.0605 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.28735 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 1.1 | 0.5 | 1.1 | 1.3 | 1 | 2
2023-04-27 | JG | MP | GW | CL | not given | 7.42 | 51.8 | 11 | not measured | 0.46 | 0.39 | not measured | 0.36 | 0.33 | not measured | not measured | 342.4 | 6.25 | 260000 | 5 | 5 | 1000 | 1 | negative | 47500 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0154 | -0.005 | -0.008 | 64.41 | -0.0003 | 2.7835 | -0.001 | 0.003 | 0.133 | 0.7555 | 1.162 | -0.005 | 32.45 | 0.016 | 2.749 | -0.001 | -0.005 | 0.081 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 6.913 | -0.001 | 22.4285 | 0.0485 | 7.39 | Not meassured | 0.334 | -0.001 | 0.0066 | 0.86552 | 0.05 | 1.0602 | 0.25 | 0.05 | 0.5 | 0.05 | 0.92573 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.29014 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 1.1 | 0.5 | 1.1 | 1.6 | 1 | 2
2023-04-27 | JG | MRT | GW | CL | not given | 7.54 | 58.6 | 14.7778 | not measured | 0.31 | 0.3 | not measured | 0.27 | 0.19 | not measured | not measured | 359.52 | 6.83 | 7500 | 5 | 5 | 1000 | 3.5 | negative | 45000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.0044 | 0.0178 | -0.005 | -0.008 | 68.37 | -0.0003 | 26.4875 | -0.001 | 0.0076 | 0.0324 | 0.778 | 1.3 | -0.005 | 34.01 | 0.0038 | 11.85 | -0.001 | -0.005 | 1.4505 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 6.048 | -0.001 | 18.884 | 0.0558 | 6.334 | Not meassured | 0.403 | -0.001 | 0.0057 | 1.5216 | 0.05 | 1.6329 | 0.25 | 0.05 | 0.5 | 0.05 | 1.7702 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.69502 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 1.2 | 0.5 | 1.1 | 0.5 | 1 | 2
2023-04-27 | JG | TANK | GW | CL | not given | 7.66 | 48.5 | 9.1667 | not measured | 0.45 | 0.34 | not measured | 0.28 | 0.23 | not measured | not measured | 376.64 | 7.05 | 5000 | 5 | 5 | 1000 | 1 | negative | 7500 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0174 | -0.005 | -0.008 | 65.72 | -0.0003 | 16.585 | -0.001 | -0.001 | 0.1478 | 0.772 | 1.25 | -0.005 | 33.85 | 0.0196 | 8.161 | 0.0012 | -0.005 | 0.929 | Not meassured | -0.002 | -0.011 | -0.005 | -0.003 | 6.372 | -0.001 | 20.499 | 0.0515 | 6.811 | Not meassured | 0.342 | -0.001 | 0.0045 | 1.1758 | 0.05 | 1.4399 | 0.25 | 0.05 | 0.5 | 0.05 | 1.66 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.62658 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 1.3 | 0.5 | 1.3 | 1.8 | 1 | 2
2023-08-30 | JG | EP | GW | CL | not given | 7.34 | 50.9 | 10.5 | 0.004 | 0.71 | 0.47 | not measured | 0.43 | 0.37 | not measured | not measured | 359.52 | 6.04 | 5000 | 5 | 5 | 1000 | 3.5 | positive | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0159 | -0.005 | -0.008 | 66.26 | -0.0003 | 3.1645 | -0.001 | -0.001 | 0.1701 | 0.8435 | 0.9447 | -0.005 | 35.56 | 0.0227 | 2.976 | -0.001 | -0.005 | -0.006 | Not meassured | -0.002 | -0.011 | Not meassured | -0.003 | 7.434 | -0.001 | 22.698 | 0.0528 | 8.151 | Not meassured | 0.374 | -0.001 | 0.008 | 0.67981 | 0.05 | 0.80907 | 0.25 | 0.05 | 0.5 | 0.05 | 0.8631 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.2385 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-08-30 | JG | MP | GW | CL | not given | 7.14 | 56.66 | 13.7 | not measured | 0.45 | 0.42 | not measured | 0.37 | 0.2 | not measured | not measured | 376.64 | 6.3 | 5000 | 5 | 5 | 1000 | 1 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0166 | -0.005 | -0.008 | 67.47 | -0.0003 | 3.918 | -0.001 | 0.0068 | 0.148 | 0.8275 | 0.9571 | -0.005 | 36.33 | 0.0168 | 3.597 | 0.001 | -0.005 | 0.1025 | Not meassured | -0.002 | -0.011 | Not meassured | -0.003 | 7.503 | -0.001 | 22.7185 | 0.0545 | 8.331 | Not meassured | 0.534 | -0.001 | 0.0072 | 0.85075 | 0.05 | 0.93149 | 0.25 | 0.05 | 0.5 | 0.05 | 0.97621 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.26037 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-08-30 | JG | MRT | GW | CL | not given | 7.43 | 65.3 | 18.5 | 0.002 | 0.29 | 0.26 | not measured | 0.19 | 0.05 | not measured | not measured | 359.52 | 6.48 | 100000 | 5 | 5 | 1000 | 4 | positive | 30000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.0167 | -0.005 | -0.008 | 67.37 | -0.0003 | 1.461 | -0.001 | 0.0148 | 0.0726 | 0.1702 | 1.478 | -0.005 | 36.22 | 0.0077 | 5.025 | 0.0016 | -0.005 | 0.0397 | Not meassured | -0.002 | -0.011 | Not meassured | -0.003 | 7.356 | -0.001 | 4.4867 | 0.0551 | 8.117 | Not meassured | 0.298 | -0.001 | 0.0091 | 2.24 | 0.05 | 1.9613 | 0.25 | 0.05 | 0.5 | 0.05 | 1.5262 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.43008 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2
2023-08-30 | JG | TANK | GW | CL | not given | 7.27 | 60.62 | 15.9 | 0.002 | 0.41 | 0.38 | not measured | 0.35 | 0.3 | not measured | not measured | 359.52 | 6.42 | 45000 | 5 | 5 | 1000 | 9 | negative | 5000 | No L colonies | Negative | Negative | 84 | 80 | 20.4 | 14 | 40 | Not measured | Not measured | 40 | Not measured | Not measured | Not measured | Not measured | Not measured | 0.004 | 0.004 | 0.016 | -0.005 | -0.008 | 66.79 | -0.0003 | 1.4002 | -0.001 | 0.0042 | 0.1488 | 0.1677 | 0.9612 | -0.005 | 35.79 | 0.0158 | 4.796 | 0.0013 | -0.005 | 0.0395 | Not meassured | -0.002 | -0.011 | Not meassured | -0.003 | 7.325 | -0.001 | 4.4962 | 0.0539 | 8.065 | Not meassured | 0.274 | -0.001 | 0.0048 | 1.2446 | 0.05 | 1.3179 | 0.25 | 0.05 | 0.5 | 0.05 | 1.2791 | 0.05 | 0.025 | 0.25 | 0.5 | 0.25 | 0.5 | 0.36032 | 0.025 | 0.5 | 0.025 | 0.025 | 0.5 | 0.025 | 0.05 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 2

## QC
Test | QC Sample Type | Frequency | Acceptane Criteria | Corrective Action
(alphabetical order)
Anions | Laboratory Fortified Blank (LFB) | 0nce after calibration, at end of run, and once every batch* | < or = +/- 15 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Quality Control Standard (QCS) (2nd Source Standard) | At least 1 per batch* End of batch QC | < or = +/- 10 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Laboratory Reagent Blank (LRB) | At least 1 per batch* | < or = to the MDL | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Precision duplicate (DUP) | Precision duplicate (DUP) | < or = +/- 10 % precision | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Laboratory Fortified Sample Matrix (LFSM) | Laboratory Fortified Sample Matrix (LFSM) | < or = +/- 15 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Continuing Calibration Check (CCC) | Continuing Calibration Check (CCC) | < or = +/- 10 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
Dissolved Oxygen | Calibrant | One every batch | 0 mg/L ±3 mg/L | Flag in comments, make new solution of calibrant
Disinfection Byproducts | Laboratory Fortified Blank (LFB) | 0nce after calibration, at end of run, and once every batch* | < or = +/- 15 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Laboratory Reagent Blank (LRB) | At least 1 per batch* | < or = to the MDL | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Precision duplicate (DUP) | Precision duplicate (DUP) | < or = +/- 10 % precision | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Laboratory Fortified Sample Matrix (LFSM) | Laboratory Fortified Sample Matrix (LFSM) | < or = +/- 15 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Continuing Calibration Check (CCC) | Continuing Calibration Check (CCC) | < or = +/- 10 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
Free Chlorine | Instrument Blank | One every batch | 0 mg/L | Flag in comments
HPC | Negative Control- Agar sterility check | One every batch | >1 CFU/ 100mL | Make fresh plates
| Method Control-blank | Every batch, If dilution is performed | >1 CFU/ 100mL | Flag in comments
Legionella (BYCE or GVPC) | Negative Control- Agar sterility check | Every Batch | >1 CFU/ 100mL | Make fresh plates
| Method Control-blank | Every batch, If dilution is performed | >1 CFU/ 100mL | Flag in comments
Metals (ICP-AES) | Laboratory Fortified Blank (LFB) | 0nce after calibration, at end of run, and once every batch* | < or = +/- 15 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Quality Control Standard (QCS) (2nd Source Standard) | one per batch* A batch is ~20 samples | < or = +/- 10 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Laboratory Reagent Blank (LRB) | one per analysis; analyte mean of last three analysis < or equal 10 % of true | < or = to the MDL | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Precision duplicate (DUP) | one per batch* | < or = +/- 10 % precision | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Laboratory Fortified Sample Matrix (LFSM) | one per batch* | < or = +/- 15 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Continuing Calibration Check (CCC) | 10 % of samples | < or = +/- 10 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
Monochlor F | Instrument Blank | One every batch | 0 mg/L | Flag in comments
Mycobacteria (7H10 or JL media) | Negative Control- Agar sterility check | One every batch | >1 CFU/ 100mL | Make fresh plates
| Method Control | One every batch | >1 CFU/ 100mL | Flag in comments
pH | Calibration | One every batch | >90% slope | Repeat with fresh calibrants
qPCR | Positive Control | One every batch (96 well plate) | Cq signal greater than threshold | DNA has degraded, use new standard, fix instrument
| Negative Control | One every batch (96 well plate) | No Cq signal greater than threshold | Assay mix contaminated, re-make fresh mix and analyze samples again.
| Nontemplate control | One every batch (96 well plate) | No Cq signal greater than threshold | Assay mix contaminated, re-make fresh mix and analyze samples again.
| Method blank | Every batch of samples undergoing DNA extration | No Cq signal greater than threshold | Resample, do not use data
| Extraction blank | Anytime the extraction rm suspected to be contaminated | No Cq signal greater than threshold | Flag in comments, suspect rm contamination
| Inhibition Control | Every Sample | Consistant Cq signal greater than threshold Avg Cq ± 1 Cq | Dilute sample and analyze again
Total Chlorine | Instrument Blank | One every batch | 0 mg/L | Flag in comments
Total Hardness | Blank (DI water) | One every batch | >1 drop | Buy new
Total Organic Carbon/Total Nitrogen | Laboratory Fortified Blank (LFB) | 0nce after calibration, at end of run, and once every batch* | < or = +/- 15 % of true value | < or = +/- 15 % of true value
| Quality Control Standard (QCS) (2nd Source Standard) | At least 1 per batch* End of batch QC | < or = +/- 10 % of true value | < or = +/- 10 % of true value
| Laboratory Reagent Blank (LRB) | At least 1 per batch* | < or = to the MDL | < or = to the MDL
| Precision duplicate (DUP) | Precision duplicate (DUP) | < or = +/- 10 % precision | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Laboratory Fortified Sample Matrix (LFSM) | Laboratory Fortified Sample Matrix (LFSM) | < or = +/- 15 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.
| Continuing Calibration Check (CCC) | Continuing Calibration Check (CCC) | < or = +/- 10 % of true value | Assess and fix. Rerun affected samples. Flag in comments, if problem persist.